# ACUTE CARE HOSPITAL
EMERGENCY OPERATIONS PLAN
COMPLIANCE CHECKLIST

CMS Emergency Preparedness  •  Maine Requirements
Fire and Life Safety  •  Acute Care Hospital Specific

| Facility / Organization |  |
| --- | --- |
| Provider Type | Acute Care Hospital |
| Prepared By |  |
| Review Date |  |

Designed for Maine acute care hospitals. Includes provider-specific CMS emergency preparedness, the full 124-category CMS-2786R review, Maine hospital requirements, and the supplied Fire Marshal documentation crosswalk.

The Healthcare Coalition of Maine (HCC-ME) is not a regulatory agency. This checklist is a preparedness and planning resource. It does not constitute regulatory approval or guarantee compliance. Facilities remain responsible for meeting applicable federal, state, and local requirements and should consult the appropriate regulatory authorities for official guidance.

Format updated October 8 2026  •  Regulatory review October 5 2026

HOW TO USE THIS CHECKLIST A survey readiness and plan development crosswalk for Maine acute care hospitals

## Purpose

Review the Emergency Operations Plan and its supporting policies, records, training, exercises, and physical safety systems. This checklist covers emergency preparedness and related safety requirements; it is a facility review tool and does not replace complete clinical Conditions of Participation, the applicable NFPA codes, accreditation standards, or an onsite CMS or Fire Marshal survey.

| Step | Action | What to do |
| --- | --- | --- |
| 1 | Identify applicability | Complete the facility profile for every campus, building, distinct part, and separately certified site. Confirm occupancy, services, and survey jurisdiction. |
| 2 | Review CMS EP | Complete Part I using 42 CFR 482.15 and Appendix Z. Record the exact EOP, policy, attachment, or record location. |
| 3 | Review other layers | Complete Part II fire and life safety, Part III clinical and Maine requirements, and the legislative watchlist. |
| 4 | Close gaps | Assign corrective actions, owners, and due dates. Document changes, staff training, retesting, and closure. |

## Identifier key

| Identifier | Meaning |
| --- | --- |
| EP01 to EP47 | Review identifiers from the combined hospital checklist; only applicable rows are included here. E-tags identify Appendix Z survey guidance. |
| CL and hospital items | Emergency-related clinical and continuity requirements for this hospital type. |
| K tags | CMS-2786R federal fire and health care facilities survey categories; not Maine FMO identifiers. |
| ME and AH items | Maine hospital statutes and rules, code applicability, permits, and AHJ verification. |
| FM items | Every numbered item in the supplied Fire Marshal documentation list dated December 18 2024. |
| S source numbers | Linked primary sources in the source register. Source numbers retain the combined checklist numbering. |

## Checklist status definitions

Met: complete and supported by evidence. Partial: incomplete, outdated, or unsupported in part. Not Met: absent or deficient. N/A: does not apply; record the reason. A written policy alone does not establish implementation. Interview staff and observe systems as appropriate.

Source review and legislative status are retained as of October 5 2026. This October 8 edition separates provider types and changes the format. Recheck legal status and adopted editions when the facility completes its review.

| FACILITY APPLICABILITY PROFILE Complete before using the compliance tables |  |
| --- | --- |
| Field | Facility entry or determination |
| Facility legal name and campus |  |
| Maine license and CMS CCN |  |
| Provider type | Acute Care Hospital ¦ CMS Part 482 |
| EOP version and approval date |  |
| Emergency preparedness lead |  |
| Facilities and life safety lead |  |
| Accreditation and survey authority | CMS State agency or accreditor; Maine DLC; Maine FMO; local fire and code officials. |
| Buildings and occupancies | List construction date, new or existing classification, floors, smoke compartments, suites, sprinklers, and any mixed occupancies. |
| Clinical services | ☐ ED ☐ ICU ☐ Surgery ☐ Maternity ☐ Newborn care ☐ Behavioral health ☐ Pediatrics ☐ Dialysis ☐ Transplant ☐ Distinct parts ☐ Offsite services |
| Patient needs and vulnerabilities | Mobility, oxygen or ventilator dependence, pregnancy, age, language, cognitive or sensory needs, and behavioral support. |
| Emergency capacity | Licensed beds, surge assumptions, receiving capacity, transport, accessible evacuation, and utility endurance. |
| Power and fire systems | Generators, fuel, transfer switches, UPS, medical gases, alarms, sprinklers, fire pumps, HVAC, dampers, elevators, and shutoffs. |
| Waivers and approvals | Record authority, conditions, dates, expiry, permits, approved plans, and equivalencies. |
| Separate certified providers | Onsite RHC, FQHC, ESRD, SNF, ASC, and other separately certified providers need their own applicable review. |

## Applicable fire and life safety layer

☐ CMS-2786R health care occupancy  ☐ Ambulatory health care occupancy
☐ Other applicable CMS form __________  ☐ Maine FMO and local AHJ requirements
Record the applicable form and code for every separate occupancy. Hospital outpatient surgical departments require the applicable ambulatory health care review.

PART I ACUTE CARE HOSPITAL CMS EMERGENCY PREPAREDNESS 42 CFR 482.15 ¦ CMS Appendix Z

## Program governance and risk assessment

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP01 | Maintain a comprehensive all-hazards program with a plan, policies and procedures, communication plan, and training and testing. Verify leadership can describe its implementation and applicable federal, state, and local requirements. Authority: E0001; 42 CFR 482.15 | ☐ | ☐ | ☐ | ☐ |  |
| EP02 | Review and update the emergency plan at least every 2 years. Retain dated review evidence, approvals, change history, and accessible current copies. Authority: E0004; 42 CFR 482.15 (a) | ☐ | ☐ | ☐ | ☐ |  |
| EP03 | Include documented facility-based and community-based risk assessments. Record hazards, likelihood, impacts, vulnerabilities, and available community resources. Authority: E0006; 42 CFR 482.15 (a)(1) | ☐ | ☐ | ☐ | ☐ |  |
| EP04 | Link response strategies to identified hazards, including natural, human-caused, care-related, facility, utility, supply, communication, cyber, and emerging infectious disease events. Authority: E0006; 42 CFR 482.15 (a)(2) | ☐ | ☐ | ☐ | ☐ |  |
| EP05 | Address the actual patient population and people at risk. Show arrangements for their care, access, communication, mobility, clinical equipment, and support needs. Authority: E0007; 42 CFR 482.15 (a)(3) | ☐ | ☐ | ☐ | ☐ |  |
| EP06 | Identify services the facility can provide during an emergency and arrangements for essential services that cannot continue onsite. Include continuity of operations. Authority: E0007; 42 CFR 482.15 (a)(3) | ☐ | ☐ | ☐ | ☐ |  |
| EP07 | Document delegations of authority, succession, activation, decision authority, and responsibilities when usual leadership is unavailable. Authority: E0007; 42 CFR 482.15 (a)(3) | ☐ | ☐ | ☐ | ☐ |  |
| EP08 | Describe cooperation with local, tribal, regional, state, and federal preparedness officials. Verify the facility can integrate with emergency management, public health, EMS, receiving providers, and HCC partners. Authority: E0009; 42 CFR 482.15 (a)(4) | ☐ | ☐ | ☐ | ☐ |  |

## Subsistence and essential utilities

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP09 | Implement policies based on the plan, risk assessment, and communication plan. Review and update them at least every 2 years and maintain implementation evidence. Authority: E0013; 42 CFR 482.15 (b) | ☐ | ☐ | ☐ | ☐ |  |
| EP10 | Provide food and water for patients and staff during evacuation and sheltering. Verify demand calculations, dietary needs, inventories, resupply arrangements, and contingency sources. Authority: E0015; 42 CFR 482.15 (b)(1)(i) | ☐ | ☐ | ☐ | ☐ |  |
| EP11 | Provide medical and pharmaceutical supplies, including clinically required gases, equipment, consumables, and PPE. Verify alternate suppliers and safe storage. Authority: E0015; 42 CFR 482.15 (b)(1)(i) | ☐ | ☐ | ☐ | ☐ |  |
| EP12 | Provide alternate energy to maintain safe patient temperatures and safe, sanitary storage of provisions. Verify loads, supported areas, temperature monitoring, and unsafe-condition response. Authority: E0015; 42 CFR 482.15 (b)(1)(ii)(A) | ☐ | ☐ | ☐ | ☐ |  |
| EP13 | Provide alternate energy for emergency lighting and fire detection, extinguishing, and alarms. Verify capacity, transfer, duration, and system operation. Authority: E0015; 42 CFR 482.15 (b)(1)(ii)(B–C) | ☐ | ☐ | ☐ | ☐ |  |
| EP14 | Provide sewage and waste disposal during interruptions. Verify sanitation, storage, removal, backup energy where needed, and limits for continued occupancy. Authority: E0015; 42 CFR 482.15 (b)(1)(ii)(D) | ☐ | ☐ | ☐ | ☐ |  |

## Tracking evacuation and continuity

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP15 | Track on-duty staff and sheltered patients during an emergency. If relocated, document the specific receiving facility or other destination name and location. Demonstrate a usable downtime method. Authority: E0018; 42 CFR 482.15 (b)(2) | ☐ | ☐ | ☐ | ☐ |  |
| EP16 | Plan safe evacuation around care and treatment needs, staff responsibilities, transport, destinations, and primary and alternate external communications. Verify accessible routes, patient movement resources, and refusal-to-evacuate response. Authority: E0020; 42 CFR 482.15 (b)(3) | ☐ | ☐ | ☐ | ☐ |  |
| EP17 | Provide sheltering for patients, staff, and volunteers who remain. Confirm alignment with hazards, protected areas, subsistence, utility capability, and relocation triggers. Authority: E0022; 42 CFR 482.15 (b)(4) | ☐ | ☐ | ☐ | ☐ |  |
| EP18 | Preserve medical documentation, confidentiality, security, and availability. Verify backups, accessible downtime records, transfer packets, and recovery of clinical data. Authority: E0023; 42 CFR 482.15 (b)(5) | ☐ | ☐ | ☐ | ☐ |  |
| EP19 | Address emergency staffing, volunteers, and integration of state or federally designated healthcare professionals for surge. Verify role assignment, credential verification, supervision, and personnel accountability. Authority: E0024; 42 CFR 482.15 (b)(6) | ☐ | ☐ | ☐ | ☐ |  |
| EP20 | Maintain arrangements with other hospitals, CAHs, and providers to receive patients during service limitation or cessation. Verify care capabilities, acceptance process, transport, and backup receiving options. Authority: E0025; 42 CFR 482.15 (b)(7) | ☐ | ☐ | ☐ | ☐ |  |
| EP21 | Describe the facility role at an alternate care site identified by emergency management under a Section 1135 waiver. Verify authorization, permitted services, personnel, supplies, records, transport, coordination, and termination of the arrangement. Authority: E0026; 42 CFR 482.15 (b)(8) | ☐ | ☐ | ☐ | ☐ |  |

## Communication plan

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP22 | Maintain a written communication plan consistent with federal, state, and local law. Review and update at least every 2 years; retain evidence of the review. Authority: E0029; 42 CFR 482.15 (c) | ☐ | ☐ | ☐ | ☐ |  |
| EP23 | Maintain names and contact information for staff, entities providing services under arrangement, patient physicians, other hospitals and CAHs, and volunteers. Authority: E0030; 42 CFR 482.15 (c)(1) | ☐ | ☐ | ☐ | ☐ |  |
| EP24 | Maintain contacts for federal, state, tribal, regional, and local preparedness staff and other assistance, including the State survey agency and public health. Authority: E0031; 42 CFR 482.15 (c)(2) | ☐ | ☐ | ☐ | ☐ |  |
| EP25 | Identify and demonstrate primary and alternate communication with staff and emergency management agencies. Verify access to equipment, directories, charging, and outage methods. Authority: E0032; 42 CFR 482.15 (c)(3) | ☐ | ☐ | ☐ | ☐ |  |
| EP26 | Share necessary patient information and medical documentation with other providers to maintain continuity. Verify sending, receiving, confidentiality, and downtime processes. Authority: E0033; 42 CFR 482.15 (c)(4) | ☐ | ☐ | ☐ | ☐ |  |
| EP27 | Provide a means to release evacuation-related patient information as allowed by 45 CFR 164.510(b)(1)(ii). Verify authorized roles and documentation. Authority: E0033; 42 CFR 482.15 (c)(5) | ☐ | ☐ | ☐ | ☐ |  |
| EP28 | Provide general patient condition and location information as allowed by 45 CFR 164.510(b)(4), including coordination with disaster relief and family notification. Authority: E0033; 42 CFR 482.15 (c)(6) | ☐ | ☐ | ☐ | ☐ |  |
| EP29 | Report occupancy, needs, and ability to assist to the AHJ, incident command, or designee. Verify the reporting process, designated staff, and usable forms or platforms. Authority: E0034; 42 CFR 482.15 (c)(7) | ☐ | ☐ | ☐ | ☐ |  |

## Training and exercise program

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP30 | Maintain a training and testing program tied to the plan, HVA, policies, and communication plan. Review and update at least every 2 years. Authority: E0036; 42 CFR 482.15 (d) | ☐ | ☐ | ☐ | ☐ |  |
| EP31 | Train all new and existing staff, contracted personnel, and volunteers initially and at least every 2 years, consistent with their expected roles. Retain individual or roster evidence and demonstrate staff knowledge. Authority: E0037; 42 CFR 482.15 (d)(1) | ☐ | ☐ | ☐ | ☐ |  |
| EP33 | When EP policies and procedures are significantly updated, train on the changes. Verify affected personnel, completion records, and knowledge of the revised procedure. Authority: E0037; 42 CFR 482.15 (d)(1)(v) | ☐ | ☐ | ☐ | ☐ |  |
| EP34 | Participate in an annual community full-scale exercise. If unavailable, conduct an annual individual facility functional exercise. Retain evidence of community exercise availability review and participation or the qualifying fallback. Authority: E0039; 42 CFR 482.15 (d)(2)(i) | ☐ | ☐ | ☐ | ☐ |  |
| EP35 | Conduct an additional exercise every year: another full-scale or functional exercise, a mock disaster drill, or a facilitated clinically relevant tabletop or workshop using a scenario and problem statements or questions. Authority: E0039; 42 CFR 482.15 (d)(2)(ii) | ☐ | ☐ | ☐ | ☐ |  |
| EP36 | If claiming an actual-event exemption, document a natural or human-caused emergency requiring EOP activation. It replaces only the next required full-scale or functional exercise, not the additional annual exercise. Authority: E0039; 42 CFR 482.15 (d)(2)(i)(B) | ☐ | ☐ | ☐ | ☐ |  |
| EP37 | Analyze exercises and actual emergencies, retain documentation, and revise the plan as needed. Verify participation, objectives, AAR findings, assigned improvements, and evidence that changes were implemented. Authority: E0039; 42 CFR 482.15 (d)(2)(iii) | ☐ | ☐ | ☐ | ☐ |  |

## Emergency and standby power

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP38 | Implement emergency and standby power based on the plan and subsistence policies. Verify essential loads, critical care, utility systems, sheltering needs, and evacuation contingencies. Authority: E0041; 42 CFR 482.15 (e) | ☐ | ☐ | ☐ | ☐ |  |
| EP39 | For new construction or renovation, verify generator location meets the federally incorporated NFPA 99, NFPA 101, TIAs, and NFPA 110 provisions. Retain drawings and design acceptance. Authority: 42 CFR 482.15 (e)(1) | ☐ | ☐ | ☐ | ☐ |  |
| EP40 | Implement EPSS inspections, tests, and maintenance. Verify generator and transfer switch logs, service intervals, failures, corrective actions, and retained records against the applicable code editions. Authority: 42 CFR 482.15 (e)(2); K918 | ☐ | ☐ | ☐ | ☐ |  |
| EP41 | For onsite generator fuel, document how power will remain operational during the emergency unless evacuating. Verify fuel condition, supply endurance, deliveries, access, vendor limitations, and contingencies. Authority: 42 CFR 482.15 (e)(3) | ☐ | ☐ | ☐ | ☐ |  |
| EP42 | Identify unsafe-temperature, lighting, fire protection, sanitation, and power thresholds requiring relocation or evacuation. Verify decisions are tied to actual loads and available resources. Authority: E0015; E0041 | ☐ | ☐ | ☐ | ☐ |  |
| EP43 | If using a healthcare microgrid categorical waiver, document election and eligibility, compliant design and references, and survey disclosure. Do not assume a microgrid or portable generator satisfies all EES requirements. Authority: QSO-23-11-LSC; S27 | ☐ | ☐ | ☐ | ☐ |  |

## Integrated systems and transplant programs

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP44 | If in a unified program, verify active participation by every separately certified facility, unique populations and services, individual facility HVAs, community HVA, and ability to use the system plan. Authority: E0042; 42 CFR 482.15 (f) | ☐ | ☐ | ☐ | ☐ |  |
| EP45 | Verify integrated policies, coordinated communications, and training and testing satisfy the requirements for each participating provider and site. Maintain controlled access and site-specific implementation evidence. Authority: E0042; 42 CFR 482.15 (f)(5) | ☐ | ☐ | ☐ | ☐ |  |
| EP46 | If the hospital has transplant programs, include a representative from each in program development and maintenance. Verify hospital, transplant, and OPO emergency duties and mutually agreed protocols. Authority: 482.15(g); E0002 | ☐ | ☐ | ☐ | ☐ |  |
| EP47 | For each transplant program, maintain emergency policies within the hospital program and arrangements to transfer transplant patients to other Medicare-approved transplant programs when services cease or are limited. Authority: 482.78(a)–(b); E0005; E0021 | ☐ | ☐ | ☐ | ☐ |  |

Two exercises are required each year: an annual community full-scale exercise or qualifying facility functional fallback, plus an additional qualifying exercise. Routine quarterly fire drills do not automatically satisfy Appendix Z. Any actual-event exemption replaces only the next required full-scale or functional exercise.

PART II FIRE AND LIFE SAFETY COMPLIANCE LAYERS CMS Life Safety Code review and Maine FMO or local AHJ requirements

## Federal and Maine code editions

Federal and Maine code editions are separate layers. Verify each building’s occupancy, new or existing classification, referenced standards, installation dates, permits, and waivers. Maine approval does not itself grant a CMS waiver. Federal NFPA 99 adoption excludes Chapters 7, 8, 12, and 13; Appendix Z still applies.

| Standard | Federal survey baseline | Maine posted edition |
| --- | --- | --- |
| NFPA 101 | 2012 and incorporated TIAs | 2018 |
| NFPA 99 | 2012 and incorporated TIAs | 2021 |
| NFPA 110 | 2010 and applicable references | 2022 |
| NFPA 72 | 2010 in supplied federal checklist | 2019 |
| NFPA 25 | 2011 in 2012 LSC framework | 2014 |
| NFPA 13 | 2010 in 2012 LSC framework | 2016 |
| NFPA 80 | 2010 in supplied federal checklist | 2019 |
| NFPA 10 | 2010 in 2012 LSC framework | 2018 |
| NFPA 96 | 2011 in supplied federal checklist | 2021 |

## Code and jurisdiction verification

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| AH01 | Record the classification and governing code for each inpatient, outpatient, business, assembly, and other occupancy. Apply separate survey forms or occupancy chapters where appropriate. Authority: CMS; Maine FMO; local AHJ | ☐ | ☐ | ☐ | ☐ |  |
| AH02 | Record existing versus new occupancy, alterations, construction type, approved plans, sprinkler coverage, rated barriers, and permits. Verify all approval conditions. Authority: S09; S12; permits | ☐ | ☐ | ☐ | ☐ |  |
| AH03 | Retain written waiver or equivalency scope, conditions, dates, and authority. Validate continuing applicability and corrective actions; do not treat a recommended waiver as granted. Authority: CMS waiver; FMO equivalency | ☐ | ☐ | ☐ | ☐ |  |

PART II A FULL CMS K TAG REVIEW All 124 unique categories in the supplied CMS-2786R healthcare form

Each row is a review prompt. Use the linked official form and applicable codes for exact measurements, exceptions, permitted alternatives, and testing conditions before marking Met. Retain plans, measurements, inventories, test reports, approvals, observed operation, and staff interview evidence. Other categories capture provisions not otherwise listed. Additional occupancy forms may apply.

## Construction and occupancy

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K100 | General Requirements – Other. Review all remaining general LSC provisions, approved equivalencies, and building documentation; record any requirement not captured by another K-tag. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K111 | Building Rehabilitation. Classify rehabilitation work and verify the applicable NFPA 101 Chapter 43 pathway, permits, construction protections, and acceptance records. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K112 | Sprinkler Requirements for Major Rehabilitation. For major rehabilitation, verify required sprinkler coverage and limits of affected areas against approved plans and applicable new-occupancy rules. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K131 | Multiple Occupancies – Sections of Health Care Facilities. Verify health care occupancy classification and permitted mixed uses; confirm the correct chapters apply to each part of the facility. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K132 | Multiple Occupancies – Contiguous Non-Health Care Occupancies. Verify separation or permitted treatment of contiguous non-healthcare occupancies; inspect barriers, openings, and shared egress. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K133 | Multiple Occupancies – Construction Type. Verify construction requirements where multiple occupancies share the building; retain approved construction and separation determinations. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K161 | Building Construction Type and Height. Verify permitted construction type and height for new or existing occupancy; retain building certification and inspect rated structural protection. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K162 | Roofing Systems Involving Combustibles. Verify permitted combustible roofing and supports, including applicable protection, separation, and existing or new provisions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K163 | Interior Nonbearing Wall Construction. Verify nonbearing interior walls and partitions meet applicable construction and fire protection requirements. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Means of egress

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K200 | Means of Egress Requirements – Other. Review additional means-of-egress provisions, accessibility, and unusual configurations not otherwise captured. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K211 | Means of Egress – General. Keep required egress continuously usable and unobstructed. Verify arrangement, furnishings, projections, and permitted wheeled equipment conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K221 | Patient Sleeping Room Doors. Verify sleeping-room doors, permitted locking, latching, and emergency opening arrangements do not prevent rapid rescue or relocation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K222 | Egress Doors. Inspect egress door locks and releases, including clinical or security locking, special-needs locking, delayed egress, and access control; test all required release conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K223 | Doors with Self-Closing Devices. Verify required self-closing doors and approved hold-open releases; inspect operation during alarm and power interruption. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K224 | Horizontal-Sliding Doors. Verify any horizontal sliding doors meet permitted use, supervision, opening, and release requirements. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K225 | Stairways and Smokeproof Enclosures. Inspect stairs and smokeproof enclosures for required protection, dimensions, continuity, and door operation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K226 | Horizontal Exits. Verify horizontal exit barriers, openings, refuge capacity, and egress from both sides; align with relocation routes. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K227 | Ramps and Other Exits. Inspect ramps and other exits for compliant construction, slope, guards, and usable discharge. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K231 | Means of Egress Capacity. Verify egress capacity calculations for the actual patient and occupant loads, including surge and relocation assumptions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K232 | Aisle, Corridor or Ramp Width. Measure clear aisle, corridor, and ramp widths; verify permitted obstructions against the applicable occupancy provisions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K233 | Clear Width of Exit and Exit Access Doors. Measure clear exit and exit-access door widths and verify the correct new or existing requirements and exceptions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K241 | Number of Exits – Story and Compartment. Verify the required number and separation of exits for every story and compartment. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K251 | Dead-End Corridors and Common Path of Travel. Measure dead ends and common paths of travel; verify applicable limits, sprinkler conditions, and permitted exceptions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K252 | Number of Exits – Corridors. Verify corridor exit arrangements and access to appropriately separated exits. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K253 | Number of Exits – Patient Sleeping and Non-Sleeping Rooms. Verify exit numbers and arrangements for patient sleeping and nonsleeping rooms, including room size and occupancy conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K254 | Corridor Access. Verify room-to-corridor access, permitted intervening rooms, and clinical arrangements against approved plans. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K255 | Suite Separation, Hazardous Content, and Subdivision. Verify suite boundaries, separation, hazardous contents, and subdivision; confirm approved suite configuration matches use. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K256 | Sleeping Suites. Verify sleeping-suite area, patient supervision, exits, and internal travel distances. Record suite areas on life safety drawings. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K257 | Non-Sleeping Suites. Verify nonsleeping-suite area, exits, internal travel, and any sprinkler or special-protection conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K261 | Travel Distance to Exits. Measure travel distances from rooms and suites to exits using actual routes and the applicable sprinkler conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K271 | Discharge from Exits. Verify exits discharge safely to a public way, with usable walking surfaces, weather maintenance, and compliant intervening spaces. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K281 | Illumination of Means of Egress. Verify normal means-of-egress illumination throughout required routes and discharge areas. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K291 | Emergency Lighting. Inspect and test emergency lighting, batteries, power supply, duration, and records against the applicable code. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K292 | Life Support Means of Egress. For life-support areas, verify required egress and emergency lighting supply; do not rely on an unsupported single route. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K293 | Exit Signage. Verify required exit signs, direction, visibility, illumination, and backup power. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Protection and alarm systems

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K300 | Protection – Other. Review other fire protection provisions and record unlisted hazards or deficiencies with the controlling citation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K311 | Vertical Openings – Enclosure. Verify enclosure of vertical openings, penetrations, shafts, stairs, and permitted exceptions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K321 | Hazardous Areas – Enclosure. Verify hazardous areas, including storage, soiled linen, waste, fuel, and mechanical areas, have the required separation, doors, or sprinkler protection. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K322 | Laboratories. Verify laboratory hazard classification and required fire protection, flammable-liquid controls, separation, and NFPA 45 conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K323 | Anesthetizing Locations. Verify anesthetizing-area medical gas valves and alarms, essential power, ventilation, temperature and humidity conditions, and applicable equipment instructions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K324 | Cooking Facilities. Inspect cooking protection, exhaust and hood systems, extinguishing equipment, fuel shutoff, and permitted residential cooking arrangements. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K325 | Alcohol Based Hand Rub Dispenser (ABHR). Verify alcohol hand-rub dispenser locations, spacing, capacity, ignition-source clearance, storage, and protection against inappropriate access. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K331 | Interior Wall and Ceiling Finish. Verify interior wall and ceiling finish classifications and testing or product evidence for installed materials. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K332 | Interior Floor Finish. Verify interior floor finish classifications for corridors, exits, and other regulated areas. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K341 | Fire Alarm System – Installation. Verify alarm installation, required system coverage, power supplies, initiating devices, monitoring, and acceptance documents. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K342 | Fire Alarm System – Initiation. Verify required manual and automatic alarm initiation, device location, accessibility, and alarm transmission. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K343 | Fire Alarm – Notification. Verify occupant and staff notification, required signals, annunciation, and response arrangements. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K344 | Fire Alarm – Control Functions. Test required alarm controls, including door release, HVAC interfaces, smoke control, elevator recall, and other linked systems. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K345 | Fire Alarm System – Testing and Maintenance. Maintain approved fire alarm inspection, testing, and maintenance records, including annual functional testing and applicable device-specific intervals. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K346 | Fire Alarm – Out of Service. For required alarms unavailable over 4 hours in 24 hours, notify the AHJ and evacuate or provide an approved fire watch; record coverage, patrols, restoration, and earlier AHJ conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K347 | Smoke Detection. Verify required smoke detection and sensitivity testing, including alarm-control locations and permitted detection arrangements. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K351 | Sprinkler System – Installation. Verify required sprinkler coverage, system design, permitted exceptions, exterior canopies, obstruction clearance, and spare components. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K352 | Sprinkler System – Supervisory Signals. Verify sprinkler supervisory signals, valve supervision, waterflow detection, and annunciation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K353 | Sprinkler System – Maintenance and Testing. Maintain sprinkler and standpipe inspection, testing, maintenance, deficiency corrections, and records, including relevant quarterly, annual, 3-year, and 5-year tasks. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K354 | Sprinkler System – Out of Service. For sprinkler impairment, determine scope and risks and notify required authorities. Over 10 hours in 24 hours, evacuate the affected area or provide an approved fire watch until restored. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K355 | Portable Fire Extinguishers. Verify appropriate extinguishers, placement, access, inspections, maintenance, and applicable internal service or hydrostatic test records. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Corridor and compartment protection

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K361 | Corridors – Areas Open to Corridor. Verify conditions for areas open to corridors, including permitted waiting, nursing, treatment, and other spaces. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K362 | Corridors – Construction of Walls. Verify corridor wall construction, continuity, rated or permitted nonrated conditions, and penetrations. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K363 | Corridor – Doors. Verify corridor doors close and latch as required, fit openings, resist smoke passage, and have only permitted exceptions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K364 | Corridor – Openings. Verify corridor openings and transfer grilles comply with the applicable limitations and protection. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K371 | Subdivision of Building Spaces – Smoke Compartments. Verify required smoke compartment number, size, arrangement, travel distance, and separation by approved drawings and observation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K372 | Subdivision of Building Spaces – Smoke Barrier Construction. Inspect smoke barrier continuity and penetrations, including concealed spaces, ducts, dampers, and firestop systems. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K373 | Subdivision of Building Spaces – Accumulation Space. Verify sufficient accumulation or refuge space on both sides of smoke barriers for relocated patients and other occupants. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K374 | Subdivision of Building Spaces – Smoke Barrier Doors. Inspect smoke barrier doors, closing and latching where required, glazing, clearance, meeting edges, and permitted configurations. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K379 | Smoke Barrier Door Glazing. Verify glazing in smoke barrier doors has the required ratings or protection and is correctly installed. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K381 | Sleeping Room Outside Windows and Doors. Verify outside sleeping-room windows or doors, with applicable sill height and exceptions; apply hospital statutory and regulatory conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Special provisions and building services

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K400 | Special Provisions – Other. Review additional special provisions and identify any Chapter 18 or 19 conditions not otherwise captured. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K421 | High-Rise Buildings. For high-rise buildings, verify required sprinkler, alarm, smoke control, egress, and emergency provisions and their inspection records. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K500 | Building Services – Other. Review remaining building-service requirements and link service failures to utility response procedures. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K511 | Utilities – Gas and Electric. Verify gas and electrical utility installations, shutoffs, labeling, protection, and code compliance. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K521 | HVAC. Verify HVAC installation, shutoffs, fire and smoke dampers, inspections, testing, and maintenance. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K522 | HVAC – Any Heating Device. Verify heating devices meet required installation, location, combustion, and protection conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K523 | HVAC – Suspended Unit Heaters. Inspect suspended unit heaters for permitted locations and protections, including separation from patient and combustible hazards. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K524 | HVAC – Direct-Vent Gas Fireplaces. For direct-vent gas fireplaces, verify permitted locations, barriers, equipment, and safeguards. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K525 | HVAC – Solid Fuel-Burning Fireplaces. For solid-fuel fireplaces, verify separation from sleeping areas, compliant enclosure, heat resistance, and required carbon monoxide detection. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K531 | Elevators. Verify elevator fire service operation, recall, hoistway protection, inspection records, and evacuation restrictions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K532 | Escalators, Dumbwaiters, and Moving Walks. Verify protection and permitted use of escalators, dumbwaiters, and moving walks, including opening enclosures. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K541 | Rubbish Chutes, Incinerators, and Laundry Chutes. Verify chute, incinerator, and laundry-shaft protection, discharge rooms, sprinklers, and door operation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Operating features and fire response

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K700 | Operating Features – Other. Review additional operating features and staffing practices not covered by another K-tag. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K711 | Evacuation and Relocation Plan. Maintain a written fire protection, relocation, and evacuation plan with prompt reporting, alarm activation, containment, extinguishment, rescue, staff duties, and fire-department cooperation; verify accessibility and staff instruction. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K712 | Fire Drills. Conduct fire drills at least quarterly on each shift, at varied expected and unexpected times, with alarm transmission and simulated fire conditions. Retain shift, scenario, response, and improvement records. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K741 | Smoking Regulations. Maintain smoking restrictions, supervision where needed, ash disposal, signs, and permitted metal containers; verify ignition-risk controls. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K751 | Draperies, Curtains, and Loosely Hanging Fabrics. Verify flame-resistance evidence and permitted use of drapes, curtains, and hanging fabrics. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K752 | Upholstered Furniture and Mattresses. Verify applicable testing, product evidence, and protection for upholstered furniture and mattresses. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K753 | Combustible Decorations. Verify decoration combustibility, limits, locations, and documentation of allowed materials. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K761 | Maintenance, Inspection & Testing - Doors. Inspect and test required fire door assemblies annually using qualified personnel and written records. Routinely inspect other corridor and smoke barrier doors; do not automatically treat every door as an annual NFPA 80 fire door. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K754 | Soiled Linen and Trash Containers. Verify linen and trash container capacity, density, hazardous-area storage, and applicable recycling exceptions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K771 | Engineer Smoke Control Systems. For engineered smoke control, maintain operational testing, maintenance, trained staff, and system documentation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K781 | Portable Space Heaters. Verify restrictions on portable space heaters and any permitted use, including element temperature and approved location. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K791 | Construction, Repair, and Improvement Operations. Maintain construction, repair, and renovation safeguards, temporary egress, fire protection, hot-work controls, and NFPA 241 protections. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Health care facilities code and gas systems

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K900 | Health Care Facilities Code - Other. Review other applicable NFPA 99 requirements. Record federal exclusions of Chapters 7, 8, 12, and 13 separately from Maine obligations. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K901 | Fundamentals – Building System Categories. Maintain formal, documented risk assessments assigning building-system Categories 1 through 4; qualified personnel determine the risk of system failure. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K902 | Gas and Vacuum Piped Systems – Other. Review remaining medical gas and vacuum Chapter 5 provisions not addressed by specific tags. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K903 | Gas and Vacuum Piped Systems – Categories. Verify medical gas, vacuum, WAGD, and air system categories match clinical risk and permitted sedation or anesthesia use. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K904 | Gas and Vacuum Piped Systems – Warning Systems. Verify required medical gas and vacuum master, area, and local warning systems and staff response to abnormal conditions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K905 | Gas and Vacuum Piped Systems – Central Supply System. Verify central supply design, source equipment, reserve supply, access, separation, and protection. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K906 | Gas and Vacuum Piped Systems – Central Supply System Operations. Verify safe central supply operations and continuity under source failure, maintenance, and reserve depletion. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K907 | Gas and Vacuum Piped Systems – Maintenance Program. Maintain medical gas and vacuum maintenance policies, equipment inventories, schedules, qualified personnel, and service records. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K908 | Gas and Vacuum Piped Systems – Inspection and Testing Operations. Verify inspection and testing of medical gas and vacuum components, alarms, safety devices, and corrective actions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K909 | Gas and Vacuum Piped Systems – Information and Warning Signs. Verify medical gas and vacuum warning signs, instructions, and required information at sources, valves, and outlets. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K910 | Gas and Vacuum Piped Systems – Modifications. For medical gas modifications, retain permits, qualified installer and verifier records, testing, and acceptance before clinical use. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Electrical systems and equipment

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K911 | Electrical Systems – Other. Review remaining electrical system Chapter 6 provisions, protections, and required electrical system documentation. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K912 | Electrical Systems – Receptacles. Verify correct receptacle type, location, grounding, and identification at patient beds and anesthetizing locations. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K913 | Electrical Systems – Wet Procedure Locations. Maintain wet-procedure location risk determinations and required isolated power or ground-fault protection, including tests. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K914 | Electrical Systems – Maintenance and Testing. Test receptacles after installation or repair and at applicable intervals. Nonhospital-grade patient-bed and anesthetizing-location receptacles require intervals not exceeding 12 months; document hospital-grade schedules. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K915 | Electrical Systems – Essential Electric System Categories. Verify essential electric system type and branches match clinical use, life-support needs, and formal risk categorization. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K916 | Electrical Systems – Essential Electric System Alarm Annunciator. Verify essential-power alarm annunciation, monitoring location, staffed response, and system testing. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K917 | Electrical Systems – Essential Electric System Receptacles. Distinctively mark receptacles or cover plates supplied from life safety and critical branches; verify patient-care staff can identify them. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K918 | Essential electrical system maintenance and testing. Verify life safety and critical branch power within 10 seconds; annually confirm when monthly tests do not demonstrate it. Record weekly generator inspections, 30-minute load tests 12 times annually at 20–40-day intervals, applicable 36-month 4-hour and supplemental load tests, transfer-switch tests, annual main/feeder breaker inspections, NFPA 111 stored-energy tests, and circuit identification. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K919 | Electrical Equipment – Other. Review other electrical equipment Chapter 10 requirements and electrical safety controls. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K920 | Electrical Equipment – Power Cords and Extension Cords. Inspect power strips, special-purpose relocatable power taps, extension cords, and power cords for listing, permitted use, rating, grounding, damage, and prohibited daisy chaining. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K921 | Electrical Equipment – Testing and Maintenance Requirements. Maintain electrical equipment inspections and tests, inventories, qualified staff, records, and safe removal of defective equipment. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

## Gas equipment and special fire protection

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K922 | Gas Equipment – Other. Review remaining gas equipment Chapter 11 provisions, safe handling, and emergency response. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K923 | Gas Equipment – Cylinder and Container Storage. Verify medical gas cylinder quantities, secure storage, separation, ventilation, signs, ignition precautions, and empty versus full identification. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K924 | Gas Equipment – Testing and Maintenance Requirements. Inspect and maintain gas equipment according to the required program and manufacturer guidance; retain records and qualified-service evidence. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K925 | Gas Equipment – Respiratory Therapy Sources of Ignition. Control ignition sources where respiratory therapy and oxygen equipment are used. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K926 | Gas Equipment – Qualifications and Training of Personnel. Verify qualifications and training of staff handling gas equipment and emergency shutoffs. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K927 | Gas Equipment – Transfilling Cylinders. Where cylinders are transfilled, verify approved room, ventilation, equipment, signage, separation, and qualified personnel. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K928 | Gas Equipment – Labeling Equipment and Cylinders. Verify required equipment and cylinder labeling, identification, and legibility. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K929 | Oxygen cylinder handling precautions. Verify safe cylinder handling, transport, securement, connections, valve practices, and oxygen precautions. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K930 | Gas Equipment – Liquid Oxygen Equipment. For liquid oxygen, verify installation, transfer and storage safeguards, trained staff, and emergency procedures. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K931 | Hyperbaric Facilities. If hyperbaric services are offered, verify applicable NFPA 99 Chapter 14 safeguards, operation, training, and emergency measures. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K932 | Features of Fire Protection – Other. Review remaining NFPA 99 fire protection provisions not otherwise captured. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |
| K933 | Features of Fire Protection – Fire Loss Prevention in Operating Rooms. Maintain operating-room fire prevention, staff training, ignition and oxygen controls, fire-response procedures, and required periodic reviews and evaluations. Authority: CMS-2786R | ☐ | ☐ | ☐ | ☐ |  |

PART II B FIRE MARSHAL DOCUMENTATION READINESS Crosswalk of all 21 items in the supplied December 18 2024 documentation list

Apply current Maine editions and permit conditions in addition to the federal survey framework. The supplied list uses some older federal referenced editions. The NFPA 66 typographic reference in that list should be checked against the relevant NFPA 99 electrical requirement.

## Required evidence packet

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| FM01 | Life safety drawings show exits, 1-hour and 2-hour barriers, horizontal exits, smoke barriers and compartments, suites, and travel distances. Verify current as-built accuracy. Cross reference K161; K226; K255–257; K261; K371–374. Authority: Original item 1 | ☐ | ☐ | ☐ | ☐ |  |
| FM02 | Sprinkler reports cover applicable quarterly, 3-year, and 5-year tasks and other required NFPA 25 component intervals. Retain repairs, acceptance, and system design records. Cross reference K351–354. Authority: Original item 2 | ☐ | ☐ | ☐ | ☐ |  |
| FM03 | Annual fire alarm functional reports and all other applicable device inspection and test intervals; record component inventory, deficiencies, and closure. Cross reference K341–346. Authority: Original item 3 | ☐ | ☐ | ☐ | ☐ |  |
| FM04 | Smoke detector sensitivity testing at the required intervals and accepted method; identify device locations and due dates. Cross reference K347; NFPA 72. Authority: Original item 4 | ☐ | ☐ | ☐ | ☐ |  |
| FM05 | Fire damper inventory, access, initial testing, and recurring test records; hospital interval generally 6 years after the first-year test. Cross reference K521; NFPA 80. Authority: Original item 5 | ☐ | ☐ | ☐ | ☐ |  |
| FM06 | Smoke damper inventory, initial testing, and recurring test records; hospital interval generally 6 years after the first-year test. Cross reference K521; NFPA 105. Authority: Original item 6 | ☐ | ☐ | ☐ | ☐ |  |
| FM07 | Medical gas inspection and test reports, including annual report requested by the checklist, component maintenance, alarm tests, and corrections. Cross reference K903–910. Authority: Original item 7 | ☐ | ☐ | ☐ | ☐ |  |
| FM08 | Annual required fire-door inspection and testing records; inspector qualification or training evidence; repair closure; routine other-door inspection. Cross reference K761. Authority: Original item 8 | ☐ | ☐ | ☐ | ☐ |  |
| FM09 | Generator weekly, monthly, and applicable annual inspection reports; transfer switches, fuel, load tests, supplemental tests, and applicable 36-month test. Cross reference E0041; K918. Authority: Original item 9 | ☐ | ☐ | ☐ | ☐ |  |
| FM10 | Nonhospital-grade patient-bed receptacle tests at intervals no greater than 12 months; identify applicable anesthetizing locations and documented schedules for other receptacles. Cross reference K914. Authority: Original item 10 | ☐ | ☐ | ☐ | ☐ |  |
| FM11 | Smoking policy and safe ash-disposal or self-closing metal-container arrangements where smoking is allowed; observe implementation. Cross reference K741. Authority: Original item 11 | ☐ | ☐ | ☐ | ☐ |  |
| FM12 | Quarterly fire drill records for each shift, varied conditions, alarm transmission, evaluations, and corrective actions. Cross reference K712. Authority: Original item 12 | ☐ | ☐ | ☐ | ☐ |  |
| FM13 | Kitchen hood, exhaust, and suppression inspection and service reports at system-specific intervals; include cleaning and fuel shutoff. Cross reference K324; NFPA 96. Authority: Original item 13 | ☐ | ☐ | ☐ | ☐ |  |
| FM14 | Portable extinguisher inspections, annual maintenance, and applicable internal-service and hydrostatic test records. Cross reference K355; NFPA 10. Authority: Original item 14 | ☐ | ☐ | ☐ | ☐ |  |
| FM15 | If hyperbaric services are present, maintain system, operational, training, and emergency evidence for the applicable code. Cross reference K931. Authority: Original item 15 | ☐ | ☐ | ☐ | ☐ |  |
| FM16 | Complete EP program and Appendix Z evidence: HVA, plan, policies, communications, training, exercises, agreements, power plan, and corrections. Cross reference Part One. Authority: Original item 16 | ☐ | ☐ | ☐ | ☐ |  |
| FM17 | Verify required detection protecting fire alarm equipment or control locations; retain detector locations and the approved system design. Cross reference K341; K347. Authority: Original item 17 | ☐ | ☐ | ☐ | ☐ |  |
| FM18 | Walkways and exit discharge are flat, usable, maintained, and continuous to the public way; inspect holes, ice, and obstructions. Cross reference K271. Authority: Original item 18 | ☐ | ☐ | ☐ | ☐ |  |
| FM19 | Evaluate exterior overhangs and canopies, including those wider than 4 feet, for required sprinkler coverage and permitted construction or protection exceptions. Cross reference K351; NFPA 13. Authority: Original item 19 | ☐ | ☐ | ☐ | ☐ |  |
| FM20 | Sleeping and nonsleeping suite areas, dimensions, boundaries, exits, and use are identified and verified on current floor plans. Cross reference K255–257. Authority: Original item 20 | ☐ | ☐ | ☐ | ☐ |  |
| FM21 | Smoke compartment number, location, square footage, travel distances, and refuge capacity are shown on plans and verified onsite. Cross reference K371–374. Authority: Original item 21 | ☐ | ☐ | ☐ | ☐ |  |

## Drills training and testing schedule

This schedule summarizes minimum or component-specific duties. Enter the adopted edition, task, last completion, and next due date in the facility maintenance system. One vendor report does not establish completion of every required interval.

| Task | Minimum or applicable interval | Evidence and authority |
| --- | --- | --- |
| EP plan, policies, communications, training program | At least every 2 years; interim changes as needed | Dated review and revisions; Part One |
| General EP staff training | Initial and at least every 2 years; significant changes | Completion and knowledge; E0037 |
| Emergency services protocols and provisions training | Annually for applicable staff | Personnel record; 482.55(c)(3) |
| Hospital transfer-policy training | Annually for relevant Part 482 hospital staff | 482.43(c); hospital-specific |
| EP exercises | Two every year | Annual full-scale or qualifying functional plus additional exercise; E0039 |
| Fire drills | At least quarterly on each shift | Alarm transmission and evaluation; K712 |
| Maine hospital security plan | Annual adoption | 22 MRS 1832; ME07 |
| State fire compliance evidence | Before license and annually under posted Ch 112 | Signed statement and corrections; ME02 |
| Generator inspections and exercise | Weekly inspection; monthly load test per applicable criteria | K918; generator and ATS logs |
| Extended generator test | Applicable Level 1 EPSS every 36 months for 4 hours | K918; NFPA 110 test method and load |
| Sprinklers and standpipes | Component schedule including quarterly, annual, 3-year and 5-year tasks | K353; NFPA 25; no single universal interval |
| Fire alarm and sensitivity tests | Annual functional report plus device-specific intervals | K345; K347; NFPA 72 |
| Required fire doors | Annual inspection and testing | K761; NFPA 80; qualified inspector |
| Fire and smoke dampers | One year after installation; then hospital interval generally 6 years | K521; applicable NFPA 80 and 105 |
| Medical gas systems | Annual report requested; component-specific maintenance and testing | K907–908; applicable NFPA 99 |
| Specified nonhospital-grade receptacles | Intervals not exceeding 12 months | K914; patient-bed and applicable anesthetizing locations |
| Portable extinguishers | Monthly visual; annual maintenance; internal and hydrostatic as applicable | K355; NFPA 10 |
| Kitchen suppression and exhaust | System and cooking-operation-specific inspection, service and cleaning | K324; do not assume one annual task covers all |
| Battery emergency lighting | Generally monthly 30-second and annual 90-minute tests or approved equivalent | K291; distinguish EES-fed lighting and self-testing alternatives |

CMS Appendix Z does not impose a universal 72-hour stock quantity. Calculate risk-based resources and evacuation thresholds and apply separate code, license, accreditation, or AHJ duration requirements. Retain records demonstrating multi-year testing and exercise improvement cycles under the facility retention policy.

PART III ACUTE CARE HOSPITAL SPECIFIC REQUIREMENTS Emergency clinical readiness and Maine hospital licensing or statutory duties

## Emergency services readiness

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| CL01 | Maintain evidence-based emergency protocols appropriate to scope, including medical, surgical, obstetrical, and immediate post-delivery emergencies. Include the response when needs exceed facility capability, even where routine obstetrical services are not offered. Authority: 482.55(c)(1) | ☐ | ☐ | ☐ | ☐ |  |
| CL02 | Verify medical staff and governing body approval, current protocol references, accessible copies, staff use, and relevant patient-record evidence. September 18 2026 guidance addresses acute care hospitals. Authority: S25; A1114 | ☐ | ☐ | ☐ | ☐ |  |
| CL03 | Keep necessary emergency medications, equipment, supplies, and blood capability available for the facility population. Check stock, expiration, maintenance, access, and ability to use emergency equipment. Authority: 482.55(c)(2); 482.27 | ☐ | ☐ | ☐ | ☐ |  |
| CL04 | Each emergency treatment area has a patient call system. Test operation and accessibility and verify the response when the system fails. Authority: 482.55(c)(2)(iii) | ☐ | ☐ | ☐ | ☐ |  |
| CL05 | Train applicable staff annually on emergency protocols and provisions. Governing body identifies staff; personnel records show completion; staff demonstrate knowledge; QAPI findings inform updates. Authority: 482.55(c)(3) | ☐ | ☐ | ☐ | ☐ |  |
| CL06 | Maintain written transfer procedures, including inpatient transfers to the required level of care, and provide annual training to relevant staff. Effective July 1 2025; this annual duty is separate from biennial EP training. Authority: 482.43(c) | ☐ | ☐ | ☐ | ☐ |  |

## Emergency care and continuity controls

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| CL07 | Address medical screening, stabilizing treatment, appropriate transfer, receiving capability and acceptance, qualified transport, records, on-call coverage, and applicable EMTALA obligations during disruption or surge. Authority: 489.20; 489.24; S28 | ☐ | ☐ | ☐ | ☐ |  |
| CL08 | Maintain fire control and evacuation procedures; state or local inspection evidence; safe equipment and facilities; ventilation and temperature controls; and continued care during utility failures. Authority: 482.41; K711 | ☐ | ☐ | ☐ | ☐ |  |
| CL09 | Coordinate outbreak recognition, isolation, PPE, cleaning, staffing, laboratory access, and public health reporting with the infection prevention program and HVA. Authority: 482.42; S29 | ☐ | ☐ | ☐ | ☐ |  |
| CL10 | Preserve and retrieve clinical records during outages and transfers. Maintain identification, orders, medication information, allergies, treatment needs, confidentiality, and system restoration procedures. Authority: 482.24; 482.15(b)(5) | ☐ | ☐ | ☐ | ☐ |  |
| CL11 | Address pharmacy, controlled drugs, cold storage, laboratory testing, blood handling, and backup services. Verify applicable CLIA and state licensure, technical policies, and outage arrangements. Authority: 482.25; 482.27; S30 | ☐ | ☐ | ☐ | ☐ |  |
| CL12 | Integrate emergency performance, patient safety events, staffing and supply failures, and corrective actions into QAPI; maintain leadership review and evidence of effectiveness. Authority: 482.21 | ☐ | ☐ | ☐ | ☐ |  |
| CL13 | Assess risks of violence, self-harm, and unsafe environments; provide appropriate staffing and training, de-escalation, protective measures, and reporting. Coordinate behavioral safety with safe egress and evacuation. Authority: 482.13(c)(2); S31; 482.15(a)(3) | ☐ | ☐ | ☐ | ☐ |  |
| CL14 | Emergency staffing preserves required qualifications, scope, supervision, and nursing coverage. Verify primary and backup rosters, credentialing, and response to unavailable personnel. Authority: 482.23 | ☐ | ☐ | ☐ | ☐ |  |

## Hospital licensing and incident reporting

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ME01 | Maintain the applicable hospital license, site and service scope, renewal, and required change notices. Authority: Ch 112 2.2, 2.5; S10–S11 | ☐ | ☐ | ☐ | ☐ |  |
| ME02 | Maintain required fire compliance statements before licensure and annually under the posted rule; retain survey and correction records. Accreditation does not exempt separate fire or complaint inspections. Authority: Ch 112 2.5.5; 22 MRS 1816 | ☐ | ☐ | ☐ | ☐ |  |
| ME03 | Report qualifying fires and emergency evacuation within 24 hours. Fires requiring patient movement, evacuation, or causing patient injury are reportable. Authority: Ch 112 1.6.2–1.6.3 | ☐ | ☐ | ☐ | ☐ |  |
| ME04 | Report suspected EMTALA violations within 72 hours using the department process. Authority: Ch 112 1.6.1 | ☐ | ☐ | ☐ | ☐ |  |
| ME05 | Report suspected abuse, neglect, or exploitation within 24 hours under this licensing rule; assess any additional mandatory reporting duties. Authority: Ch 112 1.6.4 | ☐ | ☐ | ☐ | ☐ |  |
| ME06 | Verify required building and utility plans, plumbing, water, sewer compliance, project approvals, architect certification, and FMO approval before occupancy. Authority: Ch 112 2.5.3, 2.5.7, 2.21 | ☐ | ☐ | ☐ | ☐ |  |

## Maine safety public health and service changes

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ME07 | Annually adopt a hospital safety and security plan protecting patients, visitors, and employees from aggressive or violent behavior. Provide incident and threat reporting and recording; prohibit interference with reports. Authority: 22 MRS 1832; S13 | ☐ | ☐ | ☐ | ☐ |  |
| ME08 | Notify DLC of a sentinel event within 3 business days after discovery. File the CEO-signed written report within 45 days after notification, with required event details, root cause analysis, and actions. Check the effective statute against older rule text. Authority: 22 MRS 8753; S14 | ☐ | ☐ | ☐ | ☐ |  |
| ME09 | Maintain current notifiable disease and outbreak reporting procedures, event-specific deadlines, contacts, and after-hours reporting. The amended rule became effective June 4 2025. Authority: Ch 258; S15 | ☐ | ☐ | ☐ | ☐ |  |
| ME10 | For covered business, mercantile, assembly, residential, or mixed occupancies with fuel-burning gas appliances, verify detector applicability and required installation, testing, and response. Business, mercantile, and assembly provisions began January 1 2026; determine each building occupancy. Authority: 25 MRS 2469; S16 | ☐ | ☐ | ☐ | ☐ |  |
| ME11 | Before terminating maternity or newborn services or changing the level of care, file the required notice at least 120 days in advance. Document required hospital, nursery, emergency-service, patient, and public notices. For termination, include the emergency-care plan and maternity-emergency training. Authority: PL 2025 c606; 22 MRS 1822-B; S17 | ☐ | ☐ | ☐ | ☐ |  |
| ME12 | For voluntary facility closure, follow the applicable advance notice and resident or patient protection process. Distinguish planned closure from emergency evacuation and consult DLC for the relevant procedure. Authority: 22 MRS 1822; S18 | ☐ | ☐ | ☐ | ☐ |  |

Maine’s maternity and newborn service-change notice law became effective April 3 2026. The September 30 Chapter 112 implementing proposal was still pending at the October 5 source review. Apply effective laws and distinguish proposed additions in the watchlist.

PART IV MAINE AND ACCREDITATION VERIFICATION Facility determinations and regulatory change awareness

## Verification before facility approval

Confirm the hospital license, services, building classification, current Maine and local requirements, and all approval conditions. Resolve uncertain applicability with the responsible authority and record the determination. For accredited hospitals, identify the current standards for the actual accreditation program and verify any additional emergency-management or life-safety evidence; this checklist does not reproduce those standards.

## Legislation and rulemaking watchlist

| Action |  | Status at October 5 2026 | Facility follow up |  |  |
| --- | --- | --- | --- | --- | --- |
| LD 2189 and PL 2025 c606 |  | Effective April 3 2026 | Apply the enacted maternity and newborn notice law; ME11 and S17. |  |  |
| Chapter 112 amendment |  | Proposed September 30 2026 | Monitor notice filing, proof, certification, and verification details. Hearing October 29; comments due October 30. S19. |  |  |
| Chapter 114 replacement |  | Proposed September 2 2026 | Monitor sentinel definitions and categories. Comment period closed October 2. Apply effective statute and rules meanwhile. S14 and S20. |  |  |
| LD 2100 |  | Died between houses April 7 2026 | Current fuel gas detector statute remains the authority. S16 and S24. |  |  |
| LD 1281 |  | Died on adjournment in 2026 | Proposed staffing ratios are not effective law. Continue applicable staffing requirements. S32. |  |  |
| Maine FMO rulemaking |  | No proposed rules listed at review | Monitor official notices and adopted code editions. S12 and S23. |  |  |
| CMS emergency services manuals |  | Revised September 18 2026 | Use Appendix A Rev 248 and S25 and current eCFR. |  |  |
| Date checked | Source change and facility impact |  |  | Reviewer | Action or next check |

PART V COMPLIANCE CROSSWALK AND CORRECTIVE ACTION Locate controlled evidence and track unresolved findings

## Master evidence crosswalk

| Item ID | Requirement or finding | EOP or evidence location | Status | Owner | Review or due date |
| --- | --- | --- | --- | --- | --- |

## Corrective action log

| Finding ID | Risk | Corrective action | Owner | Due date | Closure evidence |
| --- | --- | --- | --- | --- | --- |

FINAL REVIEW AND SIGN OFF Document evidence verification gap closure and leadership review

☐ Applicability confirmed  ☐ Evidence verified  ☐ Corrective actions assigned
☐ EOP revisions approved  ☐ Required training completed  ☐ Retesting documented
☐ Unresolved risk and interim measures reviewed by leadership

| Reviewer | Signature or electronic approval | Date |
| --- | --- | --- |
| Administrator or CEO |  |  |
| Medical staff or clinical leader |  |  |
| Emergency preparedness lead |  |  |
| Facilities or life safety lead |  |  |
| Nursing leader |  |  |
| Infection prevention leader |  |  |
| Quality or risk leader |  |  |

Review outcome  ☐ Gaps remain  ☐ Actions assigned  ☐ Ready for facility approval
Next formal review date __________________  Regulatory recheck date __________________

| SOURCE AND VERSION REFERENCES Primary sources retained from the October 5 2026 regulatory review |  |  |
| --- | --- | --- |
| Source | Use or version | Official link |
| S01 42 CFR 482.15 Hospital EP | Acute care EP requirements | Open source |
| S03 CMS SOM Appendix Z | Rev 204 April 16 2021; supplied copy reviewed | Open source |
| S04 42 CFR 482.41 Hospital physical environment | Federal fire and building safety | Open source |
| S06 CMS SOM Appendix A Hospitals | Rev 248 September 18 2026 | Open source |
| S08 CMS life safety and health care facilities survey hub | Federal code editions, surveys, waivers, forms | Open source |
| S09 CMS-2786R Healthcare fire survey | Supplied July 2018 form; 124 K-tag categories | Open source |
| S10 Maine DLC Hospital licensing hub | Both hospital types, licensure, construction | Open source |
| S11 10-144 CMR Chapter 112 Current hospital rule | Downloaded and read; current rule distinct from proposal | Open source |
| S12 Maine FMO adopted NFPA standards | State editions listed October 5 2026 | Open source |
| S13 22 MRS 1832 Hospital safety and security | Annual safety and security plan | Open source |
| S14 22 MRS 8753 Sentinel event reporting | Current statutory deadlines and report | Open source |
| S15 Maine CDC notifiable disease rule update | Chapter 258 effective June 4 2025; reporting hub below | Open source |
| S16 25 MRS 2469 Fuel gas detectors | Occupancy-specific requirements | Open source |
| S17 PL 2025 Chapter 606 Enacted LD 2189 | Approved April 3 2026; enacts 22 MRS 1822-B | Open source |
| S18 22 MRS 1822 Voluntary closure notice | Planned facility closure | Open source |
| S19 Proposed Chapter 112 hospital rule | Posted September 30 2026; not effective | Open source |
| S20 Proposed Chapter 114 sentinel reporting rule | Posted September 2 2026; proposal at review date | Open source |
| S21 22 MRS 1816 Inspections | Fire compliance and accreditation exceptions | Open source |
| S22 Maine FMO sprinkler shutdown policy | State impairment layer; seasonal exception not an occupied-hospital plan | Open source |
| S23 Maine FMO proposed rulemaking | No proposed rule listed on review date | Open source |
| S24 Maine Legislature LD 2100 status | Fuel gas detector bill died between houses April 7 2026 | Open source |
| S25 CMS Transmittal 248 Appendix A | September 18 2026 emergency services guidance | Open source |
| S27 CMS QSO-23-11-LSC Microgrid waiver | Conditional categorical waiver and disclosure | Open source |
| S28 42 CFR 489.24 EMTALA | Emergency screening stabilization and transfer | Open source |
| S29 Maine CDC disease reporting | Current reporting process and deadlines | Open source |
| S30 Maine DLC rules and regulations | Hospital, laboratory, and sentinel rules | Open source |
| S31 CMS QSO-23-04-Hospitals Workplace violence | Safety assessment staffing and training | Open source |
| S32 Maine Legislature 2026 disposition digest | LD 1281 Maine Quality Care Act died on adjournment | Open source |

Supplied hospital regulations, Appendix Z, CMS-2786R forms, and the Fire Marshal documentation list support the content. The attached LTC/SNF checklist supplies the layout and HCC-ME branding; LTC-specific requirements are not used as hospital requirements.

# APPENDIX A ACUTE CARE HOSPITAL POLICIES AND PROCEDURES CROSSWALK

A controlled policy, department procedure, EOP annex, or other supporting document can address a row when all applicable elements are covered and the evidence is available. Use the final two columns to record the facility document and status.

| Policy or procedure area | Checklist links | Applicable authority | Minimum elements or evidence to identify | Facility document or EOP location | Status |
| --- | --- | --- | --- | --- | --- |
| Program governance and review | EP01–02; EP09; EP22; EP30 | E0001; 42 CFR 482.15; E0004; 42 CFR 482.15 (a); E0013; 42 CFR 482.15 (b) | Maintain a comprehensive all-hazards program with a plan, policies and procedures, communication plan, and training and testing. Verify leadership can describe its implementation and applicable federal, state, and local requirements. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| HVA and hazard response strategies | EP03–04 | E0006; 42 CFR 482.15 (a)(1); E0006; 42 CFR 482.15 (a)(2) | Include documented facility-based and community-based risk assessments. Record hazards, likelihood, impacts, vulnerabilities, and available community resources. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Continuity and leadership succession | EP05–08 | E0007; 42 CFR 482.15 (a)(3) | Address the actual patient population and people at risk. Show arrangements for their care, access, communication, mobility, clinical equipment, and support needs. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Subsistence and critical supplies | EP10–14 | E0015; 42 CFR 482.15 (b)(1)(i); E0015; 42 CFR 482.15 (b)(1)(ii)(A) | Provide food and water for patients and staff during evacuation and sheltering. Verify demand calculations, dietary needs, inventories, resupply arrangements, and contingency sources. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Power fuel and critical utilities | EP38–43; K918 | E0041; 42 CFR 482.15 (e); 42 CFR 482.15 (e)(1); 42 CFR 482.15 (e)(2); K918 | Implement emergency and standby power based on the plan and subsistence policies. Verify essential loads, critical care, utility systems, sheltering needs, and evacuation contingencies. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Patient and staff accountability | EP15 | E0018; 42 CFR 482.15 (b)(2) | Track on-duty staff and sheltered patients during an emergency. If relocated, document the specific receiving facility or other destination name and location. Demonstrate a usable downtime method. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Evacuation relocation and fire response | EP16; K711 | E0020; 42 CFR 482.15 (b)(3); CMS-2786R | Plan safe evacuation around care and treatment needs, staff responsibilities, transport, destinations, and primary and alternate external communications. Verify accessible routes, patient movement resources, and refusal-to-evacuate response. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Shelter in place | EP17 | E0022; 42 CFR 482.15 (b)(4) | Provide sheltering for patients, staff, and volunteers who remain. Confirm alignment with hazards, protected areas, subsistence, utility capability, and relocation triggers. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Medical records and cyber downtime | EP18; CL10 | E0023; 42 CFR 482.15 (b)(5); 482.24; 482.15(b)(5) | Preserve medical documentation, confidentiality, security, and availability. Verify backups, accessible downtime records, transfer packets, and recovery of clinical data. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency staffing and volunteers | EP19; CL14 | E0024; 42 CFR 482.15 (b)(6); 482.23 | Address emergency staffing, volunteers, and integration of state or federally designated healthcare professionals for surge. Verify role assignment, credential verification, supervision, and personnel accountability. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Receiving facilities and transport | EP20; CL07 | E0025; 42 CFR 482.15 (b)(7); 489.20; 489.24; S28 | Maintain arrangements with other hospitals, CAHs, and providers to receive patients during service limitation or cessation. Verify care capabilities, acceptance process, transport, and backup receiving options. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Section 1135 alternate care site | EP21 | E0026; 42 CFR 482.15 (b)(8) | Describe the facility role at an alternate care site identified by emergency management under a Section 1135 waiver. Verify authorization, permitted services, personnel, supplies, records, transport, coordination, and termination of the arrangement. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Communication contact lists and reporting | EP22–29 | E0029; 42 CFR 482.15 (c); E0030; 42 CFR 482.15 (c)(1); E0031; 42 CFR 482.15 (c)(2) | Maintain a written communication plan consistent with federal, state, and local law. Review and update at least every 2 years; retain evidence of the review. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Training exercises and improvement | EP30–37 | E0036; 42 CFR 482.15 (d); E0037; 42 CFR 482.15 (d)(1); E0037; 42 CFR 482.15 (d)(1)(v) | Maintain a training and testing program tied to the plan, HVA, policies, and communication plan. Review and update at least every 2 years. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| System and transplant participation | EP44–47 | E0042; 42 CFR 482.15 (f); E0042; 42 CFR 482.15 (f)(5); 482.15(g); E0002 | If in a unified program, verify active participation by every separately certified facility, unique populations and services, individual facility HVAs, community HVA, and ability to use the system plan. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency clinical protocols and supplies | CL01–05 | 482.55(c)(1); S25; A1114; 482.55(c)(2); 482.27 | Maintain evidence-based emergency protocols appropriate to scope, including medical, surgical, obstetrical, and immediate post-delivery emergencies. Include the response when needs exceed facility capability, even where routine obstetrical services are not offered. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Hospital transfer protocol and training | CL06 | 482.43(c) | Maintain written transfer procedures, including inpatient transfers to the required level of care, and provide annual training to relevant staff. Effective July 1 2025; this annual duty is separate from biennial EP training. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Outbreak and public health response | CL09; ME09 | 482.42; S29; Ch 258; S15 | Coordinate outbreak recognition, isolation, PPE, cleaning, staffing, laboratory access, and public health reporting with the infection prevention program and HVA. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Safety security and violence reporting | CL13; ME07 | 482.13(c)(2); S31; 482.15(a)(3); 22 MRS 1832; S13 | Assess risks of violence, self-harm, and unsafe environments; provide appropriate staffing and training, de-escalation, protective measures, and reporting. Coordinate behavioral safety with safe egress and evacuation. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| State incident and sentinel reporting | ME03–05; ME08 | Ch 112 1.6.2–1.6.3; Ch 112 1.6.1; Ch 112 1.6.4 | Report qualifying fires and emergency evacuation within 24 hours. Fires requiring patient movement, evacuation, or causing patient injury are reportable. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Fire protection impairments and watches | K346; K354 | CMS-2786R | Fire Alarm – Out of Service. For required alarms unavailable over 4 hours in 24 hours, notify the AHJ and evacuate or provide an approved fire watch; record coverage, patrols, restoration, and earlier AHJ conditions. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Inspection testing and maintenance | K345; K353; K521; K761; K907–908; K918 | CMS-2786R | Fire Alarm System – Testing and Maintenance. Maintain approved fire alarm inspection, testing, and maintenance records, including annual functional testing and applicable device-specific intervals. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Construction and service change approvals | ME06; ME11–12; K791 | Ch 112 2.5.3, 2.5.7, 2.21; PL 2025 c606; 22 MRS 1822-B; S17; 22 MRS 1822; S18 | Verify required building and utility plans, plumbing, water, sewer compliance, project approvals, architect certification, and FMO approval before occupancy. |  | ☐ M ☐ P ☐ NM ☐ N/A |

# APPENDIX B ACUTE CARE HOSPITAL REGULATORY CROSSWALK

CMS EP, CMS life safety, Maine hospital licensing and statutes, and Maine FMO or local AHJ requirements are separate compliance layers. Use this navigation aid with the detailed checklist and controlling sources.

| Topic | CMS emergency preparedness or clinical authority | CMS life safety K tag layer | Maine DHHS or DLC authority | Maine FMO or local AHJ layer | Facility evidence or notes |
| --- | --- | --- | --- | --- | --- |
| Program review and HVA | 42 CFR 482.15(a); E0004–E0009 | Supports life safety and utility decisions | ME01–02; hospital license and fire compliance | Applicable state and local code layer |  |
| Subsistence and utilities | 482.15(b)(1); E0015 | K511; K521; K915–K918 | ME06 utility and construction controls | State NFPA 99 and NFPA 110 editions |  |
| Tracking evacuation and sheltering | 482.15(b)(2)–(4); E0018–E0022 | K211–K293; K371–K374; K711 | ME03 reportable fire and evacuation | State NFPA 101; local response and egress |  |
| Medical records staffing and receiving | 482.15(b)(5)–(7); E0023–E0025 | Physical systems preserve safe care | ME07 security; provider staffing duties | Safe occupancy and transfer arrangements |  |
| Communication | 482.15(c); E0029–E0034 | K341–K347 alarm and notifications | ME03–05; ME08–09 reporting | AHJ contacts and impairment notices |  |
| Training and exercises | 482.15(d); E0036–E0039 | K712 quarterly each shift; K711 fire response | ME07 annual security plan | State and AHJ conditions; no LTC drill rule |  |
| Emergency power | 482.15(e); E0041 | K915–K918; applicable NFPA 110 or 111 | ME06 plans permits and utility safety | State NFPA 99 2021; NFPA 110 2022 |  |
| Unified system | 482.15(f); E0042 | Site-specific systems and occupancies | Each licensed location and service scope | Each AHJ permit and code determination |  |
| Emergency clinical readiness | CL01–03; CL05 | K323; K933 where applicable | ME11 maternity or newborn service change | Clinical functions and safe environment |  |
| Fire protection and impairments | EP13; EP16 | K341–K355; K761 | ME02; ME03; fire compliance and incident reporting | FMO shutdown policy; local fire watches |  |
| Inspection testing and records | EP40; E0041 | K345; K353; K521; K761; K907–K918 | ME02 annual fire statement | State-adopted component requirements; FM01–21 |  |
| Safety and violence | HVA and population needs | K222 locking and releases; K711 evacuation | 22 MRS 1832; ME07 | Safe egress and approved security controls |  |
| Public health and sentinel events | HVA response and communication | Utility or safety findings may inform response | 22 MRS 8753; Ch 258; ME08–09 | Fire or utility event reporting where applicable |  |
| Service changes and closure | EP20; EP21; transfer and alternate care | K111; K791 construction protections | 22 MRS 1822; PL 2025 c606; ME11–12 | Permits approved occupancy and project review |  |
| Accreditation and waivers | Provider-specific EP duties remain applicable | AH01–AH03; granted waiver scope | License and reporting duties remain applicable | Verify current accreditation and AHJ conditions |  |
| Hospital transfer training | 482.43(c); CL06 | Safe transfer and equipment readiness | ME11 service changes where applicable | No independent substitute for clinical transfer policy |  |
| Transplant programs | 482.15(g); 482.78; EP46–47 | Applicable clinical area systems | Licensed service scope | Facility-specific gas power and fire protections |  |

Current provider-specific regulations, applicable codes, approvals, and survey guidance control. Revisit the checklist when services, buildings, hazards, laws, or CMS guidance change.