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INPATIENT HOSPICE
EMERGENCY OPERATIONS PLAN
COMPLIANCE CHECKLIST
CMS Emergency Preparedness • Maine Hospice Requirements
Hospice Operated Inpatient Facilities • Fire and Life Safety
Organization review information
	Field
	Hospice entry

	Hospice / Organization
	

	Sites / Service area
	

	Prepared by / Review date
	

	EOP version / Approval date
	


For Maine hospices that provide inpatient care directly in their own facilities. Includes shared CMS duties, inpatient emergency policies and exercises, related clinical/state requirements and the 124-category CMS health care fire safety review.
HCC-ME role
The Healthcare Coalition of Maine (HCC-ME) is not a regulatory agency. This document is a preparedness and planning resource and does not constitute regulatory approval or guarantee compliance. Each hospice remains responsible for applicable federal, state, and local requirements and should consult the appropriate regulatory authorities for official guidance.
Provider-specific edition October 14, 2026 • Source review October 13, 2026
CMS service-model distinctions confirmed October 14, 2026

	HOW TO USE THIS CHECKLIST
Hospice Operated Inpatient Facility scope and evidence review


Review the EOP, supporting policies, agreements, records, staff knowledge and safety systems. This checklist covers emergency preparedness and related compliance; the complete hospice Conditions of Participation, Maine rules, adopted codes and actual inspection directions govern detailed requirements.
Use this document when the hospice itself operates an inpatient care facility. Providing general inpatient or respite care through a contracted hospital or nursing facility is an arranged-care model governed by §418.108. If the hospice also provides home care, review the separate home-based checklist for those services.
	Step
	Action

	1
	Confirm Maine license, Medicare certification, service model, sites and applicable jurisdiction.

	2
	Review each applicable row and record the exact EOP, policy, agreement, training or inspection evidence.

	3
	Mark N/A only with a documented basis; apply optional/conditional sections to actual services and installed systems.

	4
	Assign owners and due dates, verify corrections and document review approval.


Status and authority key
Met = complete and evidenced; Partial = incomplete or unsupported in part; Not Met = absent or deficient; N/A = not applicable with a recorded reason. Review IDs support cross-reference. E-tags/K-tags are CMS identifiers; R numbers identify linked sources. Planning practices are labeled P and are not separate legal mandates.
	Scope
	Applies to

	A
	All Medicare-certified hospices

	I
	Hospice-operated inpatient facility

	C
	Arranged / contracted inpatient care

	S
	Hospice patients in SNF/NF or ICF/IID

	M
	Maine-licensed hospice

	P
	Planning practice; not a standalone mandate



	HOSPICE APPLICABILITY PROFILE
Confirm services, care settings and responsible parties

	Field
	Hospice determination / Entry

	Legal name / Maine license / CCN
	

	Sites / Service area
	

	Service model / Certification
	Hospice-operated inpatient facility
☐ General inpatient care ☐ Respite ☐ Additional home services
☐ Contracted backup inpatient care ☐ SNF/NF/ICF/IID services

	Administrator / EP lead / Clinical lead
	

	EOP version / Approval date
	

	Patients / Caregiver needs
	Mobility, cognition, language, oxygen/DME, electrical dependence, symptom relief and care goals:

	Receiving / Host facilities / Vendors
	Agreements, transport, pharmacy, DME, backup staffing and emergency contacts:

	Emergency communication
	Primary/alternate channels, call lists, reporting officials and downtime records:

	Facility capacity / Utilities
	Beds, census, staffing, transport, shelter supplies, safe care endurance and alternate energy:

	Buildings / Codes / Permits
	Occupancy, new/existing classification, CMS form, approved plans and Maine/local AHJ:

	Installed protection / Systems
	Alarms, sprinklers, medical gases, EPSS/ATS/fuel, dampers, doors, kitchens and emergency shutoffs:

	Waivers / Equivalencies
	Approving authority, written scope, conditions and validity:

	Review dates
	Plan/policy/communication review, training, exercises, applicable drills and inspections:


Required CMS exercise cycle
Conduct two exercises each year: an annual community full-scale exercise or qualifying facility functional fallback, plus an additional qualifying exercise. Any documented actual-event exemption replaces only the next required full-scale/functional exercise. Applicable quarterly fire drills are a separate requirement. Authority: §418.113(d)(3); R01/R02.

	PART I CMS HOSPICE EMERGENCY PREPAREDNESS
Hospice Operated Inpatient Facility requirements under 42 CFR 418.113


Program, risk assessment and continuity
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP01
	Maintain an implemented EP program complying with applicable federal, state and local requirements; link plan, policies, communication, training and testing.
Scope: A
Authority: R01/R02; §418.113; E0001
	☐
	☐
	☐
	☐
	

	EP02
	Maintain an emergency plan; document review and updates at least every 2 years and after changes or identified deficiencies.
Scope: A
Authority: R01/R02; §418.113(a); E0004
	☐
	☐
	☐
	☐
	

	EP03
	Document facility-based and community-based all-hazards risk assessments. Include the service area, office operations, care locations and capabilities.
Scope: A
Authority: R01/R02; §418.113(a)(1); E0006
	☐
	☐
	☐
	☐
	

	EP04
	Develop strategies for identified emergencies, including power failures, natural disasters and other hazards that could affect hospice services.
Scope: A
Authority: R01/R02; §418.113(a)(2); E0006
	☐
	☐
	☐
	☐
	

	EP05
	Describe patient population, types of services, ability to continue operations, delegation of authority and succession plans.
Scope: A
Authority: R01/R02; §418.113(a)(3); E0007
	☐
	☐
	☐
	☐
	

	EP06
	Maintain a process for cooperating and collaborating with local, tribal, regional, state and federal emergency preparedness officials to support an integrated response.
Scope: A
Authority: R01/R02; §418.113(a)(4); E0009
	☐
	☐
	☐
	☐
	


Policies, patient follow-up and home evacuation
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP07
	Base policies on the plan, HVA and communication plan; review and update at least every 2 years.
Scope: A
Authority: R01/R02; §418.113(b); E0013
	☐
	☐
	☐
	☐
	

	EP08
	Follow up with on-duty staff and patients to determine needed services during an emergency. Define contact attempts, escalation and documentation.
Scope: A
Authority: R01/R02; §418.113(b)(1); E0016
	☐
	☐
	☐
	☐
	

	EP09
	Notify state and local officials of on-duty staff or patients whom the hospice cannot contact; keep accessible reporting contacts and records.
Scope: A
Authority: R01/R02; §418.113(b)(1); E0016
	☐
	☐
	☐
	☐
	

	EP10
	Notify state and local officials about patients needing evacuation from their homes at any time because of an emergency. Evaluate medical/psychiatric needs and home conditions.
Scope: A — residential patients, if applicable
Authority: R01/R02; §418.113(b)(2); E0019
	☐
	☐
	☐
	☐
	

	EP11
	Preserve patient documentation, confidentiality and availability during downtime, relocation and emergency service disruption.
Scope: A
Authority: R01/R02; §418.113(b)(3); E0023
	☐
	☐
	☐
	☐
	

	EP12
	Plan use of hospice employees and surge staff, including integrating state/federally designated health care professionals during an emergency.
Scope: A
Authority: R01/R02; §418.113(b)(4); E0024
	☐
	☐
	☐
	☐
	

	EP13
	Arrange with other hospices or providers to receive patients when hospice operations are limited or interrupted. Identify care, transport, medication and information responsibilities.
Scope: A
Authority: R01/R02; §418.113(b)(5); E0025
	☐
	☐
	☐
	☐
	


Additional requirements for directly operated inpatient hospice
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP14
	Provide shelter in place for patients, hospice employees and volunteers remaining in the facility; define safe locations, staffing and continued care.
Scope: I
Authority: R01/R02; §418.113(b)(6)(i); E0022
	☐
	☐
	☐
	☐
	

	EP15
	Plan safe evacuation, including care/treatment needs, staff responsibilities, transport, evacuation locations and primary/alternate communication with outside assistance.
Scope: I
Authority: R01/R02; §418.113(b)(6)(ii); E0020
	☐
	☐
	☐
	☐
	

	EP16
	Provide food, water, medical and pharmaceutical supplies for patients and staff during evacuation or sheltering. Document quantities and replenishment assumptions.
Scope: I
Authority: R01/R02; §418.113(b)(6)(iii)(A); E0015
	☐
	☐
	☐
	☐
	

	EP17
	Provide alternate energy to maintain safe temperatures, protect food/medications, provide emergency lighting and maintain fire detection, extinguishing and alarm systems.
Scope: I
Authority: R01/R02; §418.113(b)(6)(iii)(B); E0015
	☐
	☐
	☐
	☐
	

	EP18
	Provide sewage and waste disposal during sheltering or evacuation; address loss of water and sanitation services.
Scope: I
Authority: R01/R02; §418.113(b)(6)(iii)(C); E0015
	☐
	☐
	☐
	☐
	

	EP19
	Address the hospice role in care at an alternate site under a declared §1135 waiver. Verify actual waiver authority, terms and site arrangements before relying on relief.
Scope: I
Authority: R01/R02; §418.113(b)(6)(iv); E0026
	☐
	☐
	☐
	☐
	

	EP20
	Track on-duty hospice employees and sheltered patients during the emergency. If relocated, document the receiving facility or other location name and location.
Scope: I
Authority: R01/R02; §418.113(b)(6)(v); E0018
	☐
	☐
	☐
	☐
	


Communication, information sharing and assistance
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP21
	Maintain a communication plan complying with federal/state/local law; review and update at least every 2 years.
Scope: A
Authority: R01/R02/R27; §418.113(c); E0029
	☐
	☐
	☐
	☐
	

	EP22
	Maintain names/contact information for hospice employees, contracted service providers, each patient’s physician and other hospices.
Scope: A
Authority: R01/R02/R27; §418.113(c)(1); E0030
	☐
	☐
	☐
	☐
	

	EP23
	Maintain contacts for federal, state, tribal, regional and local emergency preparedness staff and other assistance sources.
Scope: A
Authority: R01/R02/R27; §418.113(c)(2); E0031
	☐
	☐
	☐
	☐
	

	EP24
	Provide primary and alternate ways to communicate with hospice employees and federal/state/tribal/regional/local emergency management agencies.
Scope: A
Authority: R01/R02/R27; §418.113(c)(3); E0032
	☐
	☐
	☐
	☐
	

	EP25
	Provide a way to share needed medical documentation with other health care providers to maintain continuity of care.
Scope: A
Authority: R01/R02/R27; §418.113(c)(4); E0033
	☐
	☐
	☐
	☐
	

	EP26
	Provide a way to release patient information during evacuation consistent with 45 CFR §164.510(b)(1)(ii).
Scope: A
Authority: R01/R02/R27; §418.113(c)(5); E0033
	☐
	☐
	☐
	☐
	

	EP27
	Provide a way to communicate patients’ general condition and location consistent with 45 CFR §164.510(b)(4).
Scope: A
Authority: R01/R02/R27; §418.113(c)(6); E0033
	☐
	☐
	☐
	☐
	

	EP28
	Provide a way to communicate inpatient occupancy, needs and ability to assist to the AHJ, Incident Command Center or its designee.
Scope: I
Authority: R01/R02/R27; §418.113(c)(7); E0034
	☐
	☐
	☐
	☐
	


Training and staff knowledge
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP29
	Maintain a training and testing program based on the plan, HVA, policies and communication plan; review/update at least every 2 years.
Scope: A
Authority: R01/R02/R03; §418.113(d); E0036
	☐
	☐
	☐
	☐
	

	EP30
	Provide initial EP training consistent with roles to new/existing hospice employees, including volunteers under the employee definition, and persons providing services under arrangement.
Scope: A
Authority: R01/R02/R03; §418.113(d)(1)(i); §418.3; E0037
	☐
	☐
	☐
	☐
	

	EP31
	Demonstrate staff knowledge of emergency procedures through interview, observation or other documented evidence.
Scope: A
Authority: R01/R02/R03; §418.113(d)(1)(ii); E0037
	☐
	☐
	☐
	☐
	

	EP32
	Provide EP training at least every 2 years; keep attendance, content, roles and competency evidence.
Scope: A
Authority: R01/R02/R03; §418.113(d)(1)(iii); E0037
	☐
	☐
	☐
	☐
	

	EP33
	Periodically review and rehearse the emergency plan with hospice staff, including nonemployee staff.
Scope: A
Authority: R01/R02/R03; §418.113(d)(1)(iv); E0037
	☐
	☐
	☐
	☐
	

	EP34
	Document training and provide training on significantly updated emergency policies and procedures.
Scope: A
Authority: R01/R02/R03; §418.113(d)(1)(v)–(vi); E0037
	☐
	☐
	☐
	☐
	


Direct inpatient hospice exercise cycle
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP39
	Test the emergency plan twice per year; keep an annual calendar distinguishing the two required exercises from routine fire drills.
Scope: I
Authority: R01/R02; §418.113(d)(3); E0039
	☐
	☐
	☐
	☐
	

	EP40
	Annually participate in a community full-scale exercise, or a facility-based functional exercise when a community full-scale exercise is unavailable. Document the fallback basis.
Scope: I
Authority: R01/R02; §418.113(d)(3)(i); E0039
	☐
	☐
	☐
	☐
	

	EP41
	Conduct an additional annual qualifying community full-scale, facility functional, mock disaster drill or facilitated tabletop/workshop.
Scope: I
Authority: R01/R02; §418.113(d)(3)(ii); E0039
	☐
	☐
	☐
	☐
	

	EP42
	Document real-event activation and any exemption from the next full-scale/functional exercise. Analyze events and exercises, retain records and update the plan; the additional annual exercise remains required.
Scope: I
Authority: R01/R02; §418.113(d)(3)(i), (iii); E0039
	☐
	☐
	☐
	☐
	


Optional integrated health care system program
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	EP43
	If using an integrated program, demonstrate each separately certified facility’s active participation and account for its unique circumstances, patient population and services.
Scope: A
Authority: R01/R02; §418.113(e)(1)–(2); E0042
	☐
	☐
	☐
	☐
	

	EP44
	Demonstrate the hospice can use and implement the integrated program. Maintain a unified community HVA and each separately certified facility’s individual HVA; the plan satisfies §418.113(a)(2)–(4).
Scope: A
Authority: R01/R02; §418.113(e)(3)–(4); E0042
	☐
	☐
	☐
	☐
	

	EP45
	Maintain integrated policies/procedures, communication plan and training/testing program meeting the hospice requirements; retain facility-specific implementation evidence.
Scope: A
Authority: R01/R02; §418.113(e)(5); E0042
	☐
	☐
	☐
	☐
	



	PART II CLINICAL CONTINUITY AND MAINE HOSPICE REQUIREMENTS
Shared requirements and service-specific obligations


Hospice clinical continuity and patient protections
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	CP01
	Protect patient rights, grievances, advance directives, safety and freedom from abuse during emergencies. Preserve accessible communication and informed care decisions.
Scope: A
Authority: R03/R04; §418.52
	☐
	☐
	☐
	☐
	

	CP02
	Maintain timely initial/comprehensive assessments and reassessment, including new symptoms, psychosocial needs, caregiver capacity and emergency vulnerabilities.
Scope: A
Authority: R03/R04; §418.54
	☐
	☐
	☐
	☐
	

	CP03
	Maintain and revise individualized interdisciplinary plans of care and coordination as needs, setting, staffing or available services change.
Scope: A
Authority: R03/R04; §418.56
	☐
	☐
	☐
	☐
	

	CP04
	Maintain required 24/7 availability of nursing, physician services and drugs/biologicals; keep other covered services reasonably available as required. Maintain on-call and backup arrangements.
Scope: A
Authority: R03/R04; §418.100(c); §418.64
	☐
	☐
	☐
	☐
	

	CP05
	Maintain access to required drugs, medical supplies and DME, safe administration/storage, controlled medication procedures, and patient/family education. Arrange backups for critical equipment.
Scope: A
Authority: R03/R04; §418.106
	☐
	☐
	☐
	☐
	

	CP06
	Maintain a documented infection-control program, surveillance and education for staff, patients and caregivers; apply emergency outbreak procedures.
Scope: A
Authority: R03/R04; §418.60
	☐
	☐
	☐
	☐
	

	CP07
	Maintain complete, authenticated and confidential clinical records accessible for care. Test downtime documentation and subsequent reconciliation.
Scope: A
Authority: R03/R04; §418.104(a)–(c)
	☐
	☐
	☐
	☐
	

	CP08
	Retain clinical records at least 6 years after death/discharge unless a longer state requirement applies. If operations discontinue, notify the State agency and CMS Regional office about storage and access.
Scope: A
Authority: R03/R04; §418.104(d)
	☐
	☐
	☐
	☐
	

	CP09
	Provide required discharge/transfer summaries and records to the receiving facility or attending physician; include urgent medication and care information.
Scope: A
Authority: R03/R04; §418.104(e)
	☐
	☐
	☐
	☐
	

	CP10
	Maintain lawful discharge and election processes during disruption. Obtain the required written physician discharge order before discharge under §418.26(a); emergency relocation is not automatically revocation or discharge.
Scope: A
Authority: R03/R04; §418.26; §418.24
	☐
	☐
	☐
	☐
	

	CP11
	Use QAPI to address emergency-related adverse events, service interruptions, infections and corrective actions with governing-body oversight.
Scope: A
Authority: R03/R04; §418.58
	☐
	☐
	☐
	☐
	

	CP12
	Maintain governance, qualified staffing and service arrangements compliant with federal/state/local requirements. Verify qualifications and assigned emergency responsibilities.
Scope: A
Authority: R03/R04; §418.100; §418.114; §418.116
	☐
	☐
	☐
	☐
	


Direct inpatient hospice environment and staffing
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	IP01
	Provide staffing suited to patient volume and acuity, 24-hour nursing services and an RN providing direct care on each shift when any patient receives general inpatient care.
Scope: I
Authority: R05/R04; §418.110(a)–(b)
	☐
	☐
	☐
	☐
	

	IP02
	Maintain a safe environment, sanitation, regulated waste disposal, comfortable temperature/light/ventilation, emergency gas and water supply, and scheduled maintenance of essential emergency equipment.
Scope: I
Authority: R05/R04; §418.110(c)(1)–(4)
	☐
	☐
	☐
	☐
	

	IP03
	Apply federal NFPA 101 (2012) and NFPA 99 (2012), incorporated TIAs and approved waivers. NFPA 99 federal adoption excludes Chapters 7, 8, 12 and 13; state duties remain separate.
Scope: I
Authority: R05/R04; §418.110(d); §418.110(e)
	☐
	☐
	☐
	☐
	

	IP04
	Use positive-latching corridor doors; prohibit roller latches. Assess ABHR placement and safeguards for vulnerable patients.
Scope: I
Authority: R05/R04; §418.110(d)(1), (4)
	☐
	☐
	☐
	☐
	

	IP05
	For a sprinkler shutdown exceeding 10 hours, evacuate the affected building/portion until restored or establish a fire watch. Apply any earlier code/AHJ trigger and document notifications.
Scope: I
Authority: R05/R04; §418.110(d)(5)
	☐
	☐
	☐
	☐
	

	IP06
	Provide required outside windows/doors in sleeping rooms. Apply the 36-inch maximum sill for buildings constructed after July 5, 2016 and any documented permitted exception.
Scope: I
Authority: R05/R04; §418.110(d)(6); K381
	☐
	☐
	☐
	☐
	

	IP07
	Preserve a home-like atmosphere, privacy, family visiting/overnight arrangements, required room size and occupancy, above-grade rooms and accessible functioning call systems; record authorized waivers.
Scope: I
Authority: R05/R04; §418.110(f)–(g)
	☐
	☐
	☐
	☐
	

	IP08
	Maintain safe toilets/bathing, regulated hot water, infection prevention, sanitation, linens and sanitary dietary services consistent with patient needs.
Scope: I
Authority: R05/R04; §418.110(h)–(m)
	☐
	☐
	☐
	☐
	

	IP09
	Apply patient-rights safeguards, clinical authorization, monitoring and staff training for any restraints or seclusion; do not use them for convenience or routine evacuation control.
Scope: I
Authority: R05/R04; §418.110(n)–(o)
	☐
	☐
	☐
	☐
	

	IP10
	Maintain reporting procedures for deaths associated with restraints/seclusion and the required CMS reporting pathway and timing.
Scope: I
Authority: R05/R04; §418.110(p)
	☐
	☐
	☐
	☐
	


Arranged inpatient care and hospice in host facilities
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	CO01
	Arrange symptom-management, pain-control and respite care with participating facilities meeting the applicable requirements for that level of care, including nursing and life safety.
Scope: C
Authority: R06/R07/R01; §418.108(a)–(b)
	☐
	☐
	☐
	☐
	

	CO02
	Maintain a written agreement defining hospice oversight, plan of care, record availability, information transmission and hospice orientation of facility personnel.
Scope: C
Authority: R06/R07/R01; §418.108(c)
	☐
	☐
	☐
	☐
	

	CO03
	Maintain a signed hospice/host-facility agreement before service begins; identify patient-care responsibilities, communication, medication responsibilities and notice of relevant changes/events.
Scope: S
Authority: R06/R07/R01; §418.112(a)–(c)
	☐
	☐
	☐
	☐
	

	CO04
	Ensure required immediate abuse/neglect reporting and communication, coordinated care planning and information exchange; retain hospice professional management and designated coordination.
Scope: S
Authority: R06/R07/R01; §418.112(c)–(e)
	☐
	☐
	☐
	☐
	

	CO05
	Coordinate the hospice EOP with host-facility evacuation, sheltering, patient accountability and care continuity. Record which organization maintains building systems and supporting fire-safety records.
Scope: C / S / P
Authority: R06/R07/R01; §418.108; §418.112; §418.113
	☐
	☐
	☐
	☐
	


Maine hospice licensing and operational requirements
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	ME01
	Maintain a Maine hospice license for the approved services and scope. Non-volunteer hospice applicants must meet Maine Medicare-certification requirements; identify the volunteer-only exception.
Scope: M
Authority: R11–R17/R25; Ch.120 §2.A; 22 MRS Ch.1681
	☐
	☐
	☐
	☐
	

	ME02
	Maintain required application information and approvals, including municipal zoning/building compliance and occupancy certificate where appropriate; include electrical and fire safety approvals, applicable CLIA and biomedical-waste approvals.
Scope: M
Authority: R11–R17/R25; Ch.120 §§2.B–2.D
	☐
	☐
	☐
	☐
	

	ME03
	Notify DLC of changes in ownership, scope, address/telephone, administration or deeming status as required. Ownership changes require at least 30 days’ advance notice; the license is not transferable.
Scope: M
Authority: R11–R17/R25; Ch.120 §§2.C, 2.F
	☐
	☐
	☐
	☐
	

	ME04
	Track the actual license expiration and renewal requirements; submit renewal at least 20 days before expiration. Confirm current license terms with DLC.
Scope: M
Authority: R11–R17/R25; Ch.120 §3.C
	☐
	☐
	☐
	☐
	

	ME05
	Make records available for inspection; maintain the previous 3 years of relevant licensing/Medicare survey materials. Submit required plans of correction within 10 working days after notification.
Scope: M
Authority: R11–R17/R25; Ch.120 §3.B
	☐
	☐
	☐
	☐
	

	ME06
	Immediately report suspected abuse/neglect/exploitation through required internal and appropriate state pathways. Protect against further harm and maintain investigation/reporting records.
Scope: M
Authority: R11–R17/R25; Ch.120 §3.B(9); 22 MRS §3477
	☐
	☐
	☐
	☐
	

	ME07
	Review complaints within 2 business days; incorporate findings into quality assurance, investigate timely, and report required investigation results.
Scope: M
Authority: R11–R17/R25; Ch.120 §3.B(9)
	☐
	☐
	☐
	☐
	

	ME08
	Maintain orderly closure and continuity arrangements, organizational authority and staff orientation. Planned closure requires orderly patient-transfer arrangements at least 30 days before closure under the rule; emergency action must protect patients immediately.
Scope: M
Authority: R11–R17/R25; Ch.120 §§3.E, 4.A
	☐
	☐
	☐
	☐
	

	ME09
	Retain business records/contracts/advertising at least 5 years; maintain qualifications, licenses, orientation, education and personnel records for employed and contracted personnel. Use required identification badges or documented exceptions.
Scope: M
Authority: R11–R17/R25; Ch.120 §§4.B–4.C
	☐
	☐
	☐
	☐
	

	ME10
	Conduct quarterly clinical-record review and an annual overall provider quality-assurance review; use results to correct care and preparedness gaps.
Scope: M
Authority: R11–R17/R25; Ch.120 §4.D
	☐
	☐
	☐
	☐
	

	ME11
	Provide an interdisciplinary care plan and 24-hour, 7-day access to required hospice services; maintain nursing supervision and on-call schedules. Maintain required bereavement services.
Scope: M
Authority: R11–R17/R25; Ch.120 §§5.D–5.E
	☐
	☐
	☐
	☐
	

	ME12
	Provide at least 4 hours of orientation before direct hospice service; track required 18 hours of education, including orientation, within the first year. Apply the rule’s limited ≤20-hours-per-year exception correctly; orientation still applies.
Scope: M
Authority: R11–R17/R25; Ch.120 §§5.F–5.G
	☐
	☐
	☐
	☐
	

	ME13
	After the first year, provide at least 8 hours of continuing/in-service education annually based on hire date; keep completion records. These are general hospice education duties, separate from CMS EP training.
Scope: M
Authority: R11–R17/R25; Ch.120 §5.H
	☐
	☐
	☐
	☐
	

	ME14
	Maintain required care, meeting and discharge records. Maine’s 5-year clinical minimum does not shorten the federal 6-year death/discharge retention duty for Medicare-certified hospices.
Scope: M
Authority: R11–R17/R25; Ch.120 §§5.I–5.J; §418.104
	☐
	☐
	☐
	☐
	

	ME15
	Verify applicable Medicare certification and state eligibility for directly operated inpatient hospice; document any lawful exception with DLC rather than assuming exemption.
Scope: M
Authority: R11–R17/R25; Ch.120 §5.K; 22 MRS §8631
	☐
	☐
	☐
	☐
	

	ME16
	Maintain written home controlled-medication policy covering agency/caregiver roles, safe use/storage, expected family disposal, safe methods and access to pharmacy medication-disposal kits.
Scope: M — services in private homes, if applicable
Authority: R11–R17/R25; 22 MRS §8624(1)–(5)
	☐
	☐
	☐
	☐
	

	ME17
	Give advance notice of the post-death reminder letter; provide understandable policy education and retain the required signed acknowledgment. Send the family the disposal-reminder letter with safe-disposal information within 30 days after death.
Scope: M — services in private homes, if applicable
Authority: R11–R17/R25; 22 MRS §8624(6)–(7)
	☐
	☐
	☐
	☐
	

	ME18
	Provide required health care power-of-attorney information and maintain patient wishes, advance directives and clinically authorized care goals through relocation and handoff.
Scope: M
Authority: R11–R17/R25; Ch.120 §2.D(4); §418.52
	☐
	☐
	☐
	☐
	

	ME19
	Identify event-specific incident and notifiable-condition reporting duties, contacts, forms and deadlines. Use current DLC/CDC instructions; do not import hospital-only sentinel-event requirements without checking statutory applicability.
Scope: M
Authority: R11–R17/R25; 22 MRS Ch.1681; Maine CDC reporting
	☐
	☐
	☐
	☐
	



	PART III FIRE LIFE SAFETY AND PHYSICAL SYSTEMS
CMS Maine Fire Marshal and local code applicability


CMS inpatient hospice uses NFPA 101/99 (2012) with incorporated TIAs and specified exclusions. Maine separately posts NFPA 101 (2018), 99 (2021), 110 (2022) and other standards (R19). PL 2025 Ch.657 §3 directs NFPA 72 (2025) adoption; verify implementing rule/effective date with FMO (R37). Confirm occupancy, system categories and written approvals. State approval does not itself grant a CMS waiver.
Code applicability, permits and approvals
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	AH01
	Record occupancy, jurisdiction and applicable code/form for every hospice office, inpatient building and mixed occupancy. Do not apply the inpatient K-tag form automatically to home-based service offices or private homes.
Scope: M / I
Authority: R05/R08/R18; §418.110; occupancy-specific codes
	☐
	☐
	☐
	☐
	

	AH02
	Record new/existing classification, construction/alterations, approved plans, sprinkler coverage, barriers, permits and occupancy approvals; obtain required review before changes.
Scope: M / I
Authority: R18/R21; FMO Ch.3,4,15,17,19,20
	☐
	☐
	☐
	☐
	

	AH03
	Retain written waiver/equivalency scope, conditions, authority and validity. Maine approvals do not themselves grant a federal CMS waiver.
Scope: I
Authority: R05/R18; §418.110(d)–(e)
	☐
	☐
	☐
	☐
	

	AH04
	Determine fuel-gas detector applicability for each building, occupancy and fuel-burning appliance; document installations, testing and any legal exception.
Scope: M
Authority: R22; 25 MRS §2469
	☐
	☐
	☐
	☐
	

	AH05
	Record NFPA 99 system categories and electrical/power requirements based on risks and care delivered. Identify emergency loads, fuel endurance and alternate utilities; verify required systems with the AHJ.
Scope: I
Authority: R01/R05/R19; NFPA 99/110
	☐
	☐
	☐
	☐
	



	PART III A FULL CMS K TAG REVIEW
124 categories conditional on applicable inpatient health care occupancy


These prompts cover every unique category in CMS-2786R. Use the official form and governing codes for exact dimensions, exceptions, permitted alternatives, component intervals and testing conditions. Record the basis for any system-specific N/A. Verify additional forms for other occupancies and host facilities.
K-tag review — Construction, interior finishes and exits
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K100
	General Requirements – Other. Review all remaining general LSC provisions, approved equivalencies, and building documentation; record any requirement not captured by another K-tag.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K111
	Building Rehabilitation. Classify rehabilitation work and verify the applicable NFPA 101 Chapter 43 pathway, permits, construction protections, and acceptance records.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K112
	Sprinkler Requirements for Major Rehabilitation. For major rehabilitation, verify required sprinkler coverage and limits of affected areas against approved plans and applicable new-occupancy rules.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K131
	Multiple Occupancies – Sections of Health Care Facilities. Verify health care occupancy classification and permitted mixed uses; confirm the correct chapters apply to each part of the facility.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K132
	Multiple Occupancies – Contiguous Non-Health Care Occupancies. Verify separation or permitted treatment of contiguous non-healthcare occupancies; inspect barriers, openings, and shared egress.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K133
	Multiple Occupancies – Construction Type. Verify construction requirements where multiple occupancies share the building; retain approved construction and separation determinations.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K161
	Building Construction Type and Height. Verify permitted construction type and height for new or existing occupancy; retain building certification and inspect rated structural protection.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K162
	Roofing Systems Involving Combustibles. Verify permitted combustible roofing and supports, including applicable protection, separation, and existing or new provisions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K163
	Interior Nonbearing Wall Construction. Verify nonbearing interior walls and partitions meet applicable construction and fire protection requirements.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K200
	Means of Egress Requirements – Other. Review additional means-of-egress provisions, accessibility, and unusual configurations not otherwise captured.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K211
	Means of Egress – General. Keep required egress continuously usable and unobstructed. Verify arrangement, furnishings, projections, and permitted wheeled equipment conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K221
	Patient Sleeping Room Doors. Verify sleeping-room doors, permitted locking, latching, and emergency opening arrangements do not prevent rapid rescue or relocation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K222
	Egress Doors. Inspect egress door locks and releases, including clinical or security locking, special-needs locking, delayed egress, and access control; test all required release conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K223
	Doors with Self-Closing Devices. Verify required self-closing doors and approved hold-open releases; inspect operation during alarm and power interruption.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K224
	Horizontal-Sliding Doors. Verify any horizontal sliding doors meet permitted use, supervision, opening, and release requirements.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K225
	Stairways and Smokeproof Enclosures. Inspect stairs and smokeproof enclosures for required protection, dimensions, continuity, and door operation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K226
	Horizontal Exits. Verify horizontal exit barriers, openings, refuge capacity, and egress from both sides; align with relocation routes.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K227
	Ramps and Other Exits. Inspect ramps and other exits for compliant construction, slope, guards, and usable discharge.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K231
	Means of Egress Capacity. Verify egress capacity calculations for the actual patient and occupant loads, including surge and relocation assumptions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K232
	Aisle, Corridor or Ramp Width. Measure clear aisle, corridor, and ramp widths; verify permitted obstructions against the applicable occupancy provisions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K233
	Clear Width of Exit and Exit Access Doors. Measure clear exit and exit-access door widths and verify the correct new or existing requirements and exceptions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K241
	Number of Exits – Story and Compartment. Verify the required number and separation of exits for every story and compartment.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K251
	Dead-End Corridors and Common Path of Travel. Measure dead ends and common paths of travel; verify applicable limits, sprinkler conditions, and permitted exceptions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K252
	Number of Exits – Corridors. Verify corridor exit arrangements and access to appropriately separated exits.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K253
	Number of Exits – Patient Sleeping and Non-Sleeping Rooms. Verify exit numbers and arrangements for patient sleeping and nonsleeping rooms, including room size and occupancy conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K254
	Corridor Access. Verify room-to-corridor access, permitted intervening rooms, and clinical arrangements against approved plans.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K255
	Suite Separation, Hazardous Content, and Subdivision. Verify suite boundaries, separation, hazardous contents, and subdivision; confirm approved suite configuration matches use.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K256
	Sleeping Suites. Verify sleeping-suite area, patient supervision, exits, and internal travel distances. Record suite areas on life safety drawings.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K257
	Non-Sleeping Suites. Verify nonsleeping-suite area, exits, internal travel, and any sprinkler or special-protection conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K261
	Travel Distance to Exits. Measure travel distances from rooms and suites to exits using actual routes and the applicable sprinkler conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K271
	Discharge from Exits. Verify exits discharge safely to a public way, with usable walking surfaces, weather maintenance, and compliant intervening spaces.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K281
	Illumination of Means of Egress. Verify normal means-of-egress illumination throughout required routes and discharge areas.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K291
	Emergency Lighting. Inspect and test emergency lighting, batteries, power supply, duration, and records against the applicable code.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K292
	Life Support Means of Egress. For life-support areas, verify required egress and emergency lighting supply; do not rely on an unsupported single route.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K293
	Exit Signage. Verify required exit signs, direction, visibility, illumination, and backup power.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	


K-tag review — Hazardous areas, cooking and flammable materials
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K300
	Protection – Other. Review other fire protection provisions and record unlisted hazards or deficiencies with the controlling citation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K311
	Vertical Openings – Enclosure. Verify enclosure of vertical openings, penetrations, shafts, stairs, and permitted exceptions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K321
	Hazardous Areas – Enclosure. Verify hazardous areas, including storage, soiled linen, waste, fuel, and mechanical areas, have the required separation, doors, or sprinkler protection.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K322
	Laboratories. Verify laboratory hazard classification and required fire protection, flammable-liquid controls, separation, and NFPA 45 conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K323
	Anesthetizing Locations. Verify anesthetizing-area medical gas valves and alarms, essential power, ventilation, temperature and humidity conditions, and applicable equipment instructions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K324
	Cooking Facilities. Inspect cooking protection, exhaust and hood systems, extinguishing equipment, fuel shutoff, and permitted residential cooking arrangements.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K325
	Alcohol Based Hand Rub Dispenser (ABHR). Verify alcohol hand-rub dispenser locations, spacing, capacity, ignition-source clearance, storage, and protection against inappropriate access.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K331
	Interior Wall and Ceiling Finish. Verify interior wall and ceiling finish classifications and testing or product evidence for installed materials.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K332
	Interior Floor Finish. Verify interior floor finish classifications for corridors, exits, and other regulated areas.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	


K-tag review — Fire alarms, sprinklers and extinguishers
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K341
	Fire Alarm System – Installation. Verify alarm installation, required system coverage, power supplies, initiating devices, monitoring, and acceptance documents.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K342
	Fire Alarm System – Initiation. Verify required manual and automatic alarm initiation, device location, accessibility, and alarm transmission.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K343
	Fire Alarm – Notification. Verify occupant and staff notification, required signals, annunciation, and response arrangements.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K344
	Fire Alarm – Control Functions. Test required alarm controls, including door release, HVAC interfaces, smoke control, elevator recall, and other linked systems.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K345
	Fire Alarm System – Testing and Maintenance. Maintain approved fire alarm inspection, testing, and maintenance records, including annual functional testing and applicable device-specific intervals.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K346
	Fire Alarm – Out of Service. For required alarms unavailable over 4 hours in 24 hours, notify the AHJ and evacuate or provide an approved fire watch; record coverage, patrols, restoration, and earlier AHJ conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K347
	Smoke Detection. Verify required smoke detection and sensitivity testing, including alarm-control locations and permitted detection arrangements.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K351
	Sprinkler System – Installation. Verify required sprinkler coverage, system design, permitted exceptions, exterior canopies, obstruction clearance, and spare components.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K352
	Sprinkler System – Supervisory Signals. Verify sprinkler supervisory signals, valve supervision, waterflow detection, and annunciation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K353
	Sprinkler System – Maintenance and Testing. Maintain sprinkler and standpipe inspection, testing, maintenance, deficiency corrections, and records, including relevant quarterly, annual, 3-year, and 5-year tasks.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K354
	Sprinkler System – Out of Service. For sprinkler impairment, determine scope and risks and notify required authorities. Over 10 hours in 24 hours, evacuate the affected area or provide an approved fire watch until restored.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K355
	Portable Fire Extinguishers. Verify appropriate extinguishers, placement, access, inspections, maintenance, and applicable internal service or hydrostatic test records.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K361
	Corridors – Areas Open to Corridor. Verify conditions for areas open to corridors, including permitted waiting, nursing, treatment, and other spaces.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K362
	Corridors – Construction of Walls. Verify corridor wall construction, continuity, rated or permitted nonrated conditions, and penetrations.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K363
	Corridor – Doors. Verify corridor doors close and latch as required, fit openings, resist smoke passage, and have only permitted exceptions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K364
	Corridor – Openings. Verify corridor openings and transfer grilles comply with the applicable limitations and protection.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	


K-tag review — Corridors, smoke barriers and patient rooms
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K371
	Subdivision of Building Spaces – Smoke Compartments. Verify required smoke compartment number, size, arrangement, travel distance, and separation by approved drawings and observation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K372
	Subdivision of Building Spaces – Smoke Barrier Construction. Inspect smoke barrier continuity and penetrations, including concealed spaces, ducts, dampers, and firestop systems.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K373
	Subdivision of Building Spaces – Accumulation Space. Verify sufficient accumulation or refuge space on both sides of smoke barriers for relocated patients and other occupants.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K374
	Subdivision of Building Spaces – Smoke Barrier Doors. Inspect smoke barrier doors, closing and latching where required, glazing, clearance, meeting edges, and permitted configurations.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K379
	Smoke Barrier Door Glazing. Verify glazing in smoke barrier doors has the required ratings or protection and is correctly installed.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K381
	Sleeping Room Outside Windows and Doors. Verify outside sleeping-room windows or doors, with applicable sill height and exceptions; apply hospice §418.110(d)(6), including outside windows/doors and applicable sill-height conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	


K-tag review — Building service systems
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K400
	Special Provisions – Other. Review additional special provisions and identify any Chapter 18 or 19 conditions not otherwise captured.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K421
	High-Rise Buildings. For high-rise buildings, verify required sprinkler, alarm, smoke control, egress, and emergency provisions and their inspection records.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K500
	Building Services – Other. Review remaining building-service requirements and link service failures to utility response procedures.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K511
	Utilities – Gas and Electric. Verify gas and electrical utility installations, shutoffs, labeling, protection, and code compliance.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K521
	HVAC. Verify HVAC installation, shutoffs, fire and smoke dampers, inspections, testing, and maintenance.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K522
	HVAC – Any Heating Device. Verify heating devices meet required installation, location, combustion, and protection conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K523
	HVAC – Suspended Unit Heaters. Inspect suspended unit heaters for permitted locations and protections, including separation from patient and combustible hazards.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K524
	HVAC – Direct-Vent Gas Fireplaces. For direct-vent gas fireplaces, verify permitted locations, barriers, equipment, and safeguards.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K525
	HVAC – Solid Fuel-Burning Fireplaces. For solid-fuel fireplaces, verify separation from sleeping areas, compliant enclosure, heat resistance, and required carbon monoxide detection.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K531
	Elevators. Verify elevator fire service operation, recall, hoistway protection, inspection records, and evacuation restrictions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K532
	Escalators, Dumbwaiters, and Moving Walks. Verify protection and permitted use of escalators, dumbwaiters, and moving walks, including opening enclosures.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K541
	Rubbish Chutes, Incinerators, and Laundry Chutes. Verify chute, incinerator, and laundry-shaft protection, discharge rooms, sprinklers, and door operation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	


K-tag review — Operating features and emergency procedures
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K700
	Operating Features – Other. Review additional operating features and staffing practices not covered by another K-tag.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K711
	Evacuation and Relocation Plan. Maintain a written fire protection, relocation, and evacuation plan with prompt reporting, alarm activation, containment, extinguishment, rescue, staff duties, and fire-department cooperation; verify accessibility and staff instruction.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K712
	Fire Drills. Conduct fire drills at least quarterly on each shift, at varied expected and unexpected times, with alarm transmission and simulated fire conditions. Retain shift, scenario, response, and improvement records.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K741
	Smoking Regulations. Maintain smoking restrictions, supervision where needed, ash disposal, signs, and permitted metal containers; verify ignition-risk controls.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K751
	Draperies, Curtains, and Loosely Hanging Fabrics. Verify flame-resistance evidence and permitted use of drapes, curtains, and hanging fabrics.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K752
	Upholstered Furniture and Mattresses. Verify applicable testing, product evidence, and protection for upholstered furniture and mattresses.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K753
	Combustible Decorations. Verify decoration combustibility, limits, locations, and documentation of allowed materials.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K761
	Maintenance, Inspection & Testing - Doors. Inspect and test required fire door assemblies annually using qualified personnel and written records. Routinely inspect other corridor and smoke barrier doors; do not automatically treat every door as an annual NFPA 80 fire door.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K754
	Soiled Linen and Trash Containers. Verify linen and trash container capacity, density, hazardous-area storage, and applicable recycling exceptions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K771
	Engineer Smoke Control Systems. For engineered smoke control, maintain operational testing, maintenance, trained staff, and system documentation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K781
	Portable Space Heaters. Verify restrictions on portable space heaters and any permitted use, including element temperature and approved location.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K791
	Construction, Repair, and Improvement Operations. Maintain construction, repair, and renovation safeguards, temporary egress, fire protection, hot-work controls, and NFPA 241 protections.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	


K-tag review — Health care facility systems and equipment
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	K900
	Health Care Facilities Code - Other. Review other applicable NFPA 99 requirements. Record federal exclusions of Chapters 7, 8, 12, and 13 separately from Maine obligations.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K901
	Fundamentals – Building System Categories. Maintain formal, documented risk assessments assigning building-system Categories 1 through 4; qualified personnel determine the risk of system failure.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K902
	Gas and Vacuum Piped Systems – Other. Review remaining medical gas and vacuum Chapter 5 provisions not addressed by specific tags.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K903
	Gas and Vacuum Piped Systems – Categories. Verify medical gas, vacuum, WAGD, and air system categories match clinical risk and permitted sedation or anesthesia use.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K904
	Gas and Vacuum Piped Systems – Warning Systems. Verify required medical gas and vacuum master, area, and local warning systems and staff response to abnormal conditions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K905
	Gas and Vacuum Piped Systems – Central Supply System. Verify central supply design, source equipment, reserve supply, access, separation, and protection.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K906
	Gas and Vacuum Piped Systems – Central Supply System Operations. Verify safe central supply operations and continuity under source failure, maintenance, and reserve depletion.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K907
	Gas and Vacuum Piped Systems – Maintenance Program. Maintain medical gas and vacuum maintenance policies, equipment inventories, schedules, qualified personnel, and service records.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K908
	Gas and Vacuum Piped Systems – Inspection and Testing Operations. Verify inspection and testing of medical gas and vacuum components, alarms, safety devices, and corrective actions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K909
	Gas and Vacuum Piped Systems – Information and Warning Signs. Verify medical gas and vacuum warning signs, instructions, and required information at sources, valves, and outlets.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K910
	Gas and Vacuum Piped Systems – Modifications. For medical gas modifications, retain permits, qualified installer and verifier records, testing, and acceptance before clinical use.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K911
	Electrical Systems – Other. Review remaining electrical system Chapter 6 provisions, protections, and required electrical system documentation.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K912
	Electrical Systems – Receptacles. Verify correct receptacle type, location, grounding, and identification at patient beds and anesthetizing locations.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K913
	Electrical Systems – Wet Procedure Locations. Maintain wet-procedure location risk determinations and required isolated power or ground-fault protection, including tests.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K914
	Electrical Systems – Maintenance and Testing. Test receptacles after installation or repair and at applicable intervals. Nonhospital-grade patient-bed and anesthetizing-location receptacles require intervals not exceeding 12 months; document hospital-grade schedules.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K915
	Electrical Systems – Essential Electric System Categories. Verify essential electric system type and branches match clinical use, life-support needs, and formal risk categorization.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K916
	Electrical Systems – Essential Electric System Alarm Annunciator. Verify essential-power alarm annunciation, monitoring location, staffed response, and system testing.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K917
	Electrical Systems – Essential Electric System Receptacles. Distinctively mark receptacles or cover plates supplied from life safety and critical branches; verify patient-care staff can identify them.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K918
	Essential electrical system maintenance and testing. Verify life safety and critical branch power within 10 seconds; annually confirm when monthly tests do not demonstrate it. Record weekly generator inspections, 30-minute load tests 12 times annually at 20–40-day intervals, applicable 36-month 4-hour and supplemental load tests, transfer-switch tests, annual main/feeder breaker inspections, NFPA 111 stored-energy tests, and circuit identification.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K919
	Electrical Equipment – Other. Review other electrical equipment Chapter 10 requirements and electrical safety controls.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K920
	Electrical Equipment – Power Cords and Extension Cords. Inspect power strips, special-purpose relocatable power taps, extension cords, and power cords for listing, permitted use, rating, grounding, damage, and prohibited daisy chaining.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K921
	Electrical Equipment – Testing and Maintenance Requirements. Maintain electrical equipment inspections and tests, inventories, qualified staff, records, and safe removal of defective equipment.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K922
	Gas Equipment – Other. Review remaining gas equipment Chapter 11 provisions, safe handling, and emergency response.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K923
	Gas Equipment – Cylinder and Container Storage. Verify medical gas cylinder quantities, secure storage, separation, ventilation, signs, ignition precautions, and empty versus full identification.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K924
	Gas Equipment – Testing and Maintenance Requirements. Inspect and maintain gas equipment according to the required program and manufacturer guidance; retain records and qualified-service evidence.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K925
	Gas Equipment – Respiratory Therapy Sources of Ignition. Control ignition sources where respiratory therapy and oxygen equipment are used.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K926
	Gas Equipment – Qualifications and Training of Personnel. Verify qualifications and training of staff handling gas equipment and emergency shutoffs.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K927
	Gas Equipment – Transfilling Cylinders. Where cylinders are transfilled, verify approved room, ventilation, equipment, signage, separation, and qualified personnel.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K928
	Gas Equipment – Labeling Equipment and Cylinders. Verify required equipment and cylinder labeling, identification, and legibility.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K929
	Oxygen cylinder handling precautions. Verify safe cylinder handling, transport, securement, connections, valve practices, and oxygen precautions.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K930
	Gas Equipment – Liquid Oxygen Equipment. For liquid oxygen, verify installation, transfer and storage safeguards, trained staff, and emergency procedures.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K931
	Hyperbaric Facilities. If hyperbaric services are offered, verify applicable NFPA 99 Chapter 14 safeguards, operation, training, and emergency measures.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K932
	Features of Fire Protection – Other. Review remaining NFPA 99 fire protection provisions not otherwise captured.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	

	K933
	Features of Fire Protection – Fire Loss Prevention in Operating Rooms. Maintain operating-room fire prevention, staff training, ignition and oxygen controls, fire-response procedures, and required periodic reviews and evaluations.
Scope: I — if applicable
Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions
	☐
	☐
	☐
	☐
	



	PART III B FIRE MARSHAL EVIDENCE PACKET
Confirm facility-specific inspection requests and adopted codes


Maintain current plans, inventories, testing/maintenance reports, staff fire response and correction records. Apply each documentation category to actual systems and occupancy; retain the current Fire Marshal/local AHJ inspection request with this packet.
Fire Marshal documentation and inspection evidence
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	FM01
	Life safety drawings show exits, 1-hour and 2-hour barriers, horizontal exits, smoke barriers and compartments, suites, and travel distances. Verify current as-built accuracy. Cross reference K161; K226; K255–257; K261; K371–374.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM02
	Sprinkler reports cover applicable quarterly, 3-year, and 5-year tasks and other required NFPA 25 component intervals. Retain repairs, acceptance, and system design records. Cross reference K351–354.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM03
	Annual fire alarm functional reports and all other applicable device inspection and test intervals; record component inventory, deficiencies, and closure. Cross reference K341–346.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM04
	Smoke detector sensitivity testing at the required intervals and accepted method; identify device locations and due dates. Cross reference K347; NFPA 72.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM05
	Fire damper inventory, access, initial and recurring inspection/test reports. Determine the governing cycle for hospice occupancy; do not assume the hospital six-year exception applies. Cross reference K521; NFPA 80.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM06
	Smoke damper inventory, access, initial and recurring inspection/test reports. Document the applicable code cycle and any approved hospital exception. Cross reference K521; NFPA 105.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM07
	Medical gas component inventories, acceptance/verification, alarm tests, required maintenance and repairs. Retain annual inspection reports if required by the AHJ or system schedule. Cross reference K903–910.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM08
	Annual required fire-door inspection and testing records; inspector qualification or training evidence; repair closure; routine other-door inspection. Cross reference K761.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM09
	Generator/EPSS weekly inspections, monthly load tests, ATS tests, fuel, repairs and applicable supplemental/36-month test records. Determine applicability from system category and code. Cross reference K918 and §418.113(b)(6).
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM10
	Nonhospital-grade patient-bed receptacle tests at intervals no greater than 12 months; identify applicable anesthetizing locations and documented schedules for other receptacles. Cross reference K914.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM11
	Smoking policy and safe ash-disposal or self-closing metal-container arrangements where smoking is allowed; observe implementation. Cross reference K741.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM12
	Quarterly fire drill records for each shift, varied conditions, alarm transmission, evaluations, and corrective actions. Cross reference K712.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM13
	Kitchen hood, exhaust, and suppression inspection and service reports at system-specific intervals; include cleaning and fuel shutoff. Cross reference K324; NFPA 96.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM14
	Portable extinguisher inspections, annual maintenance, and applicable internal-service and hydrostatic test records. Cross reference K355; NFPA 10.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM15
	If hyperbaric services are present, maintain system, operational, training, and emergency evidence for the applicable code. Cross reference K931.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM16
	Complete hospice EP evidence: HVA, plan, policies, communications, patient and on-duty staff follow-up, applicable inpatient power/subsistence, training, exercises, agreements and corrections. Cross reference EP01–EP45.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM17
	Verify required detection protecting fire alarm equipment or control locations; retain detector locations and the approved system design. Cross reference K341; K347.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM18
	Walkways and exit discharge are flat, usable, maintained, and continuous to the public way; inspect holes, ice, and obstructions. Cross reference K271.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM19
	Evaluate exterior overhangs and canopies, including those wider than 4 feet, for required sprinkler coverage and permitted construction or protection exceptions. Cross reference K351; NFPA 13.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM20
	Sleeping and nonsleeping suite areas, dimensions, boundaries, exits, and use are identified and verified on current floor plans. Cross reference K255–257.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	

	FM21
	Smoke compartment number, location, square footage, travel distances, and refuge capacity are shown on plans and verified onsite. Cross reference K371–374.
Scope: I / M — system or occupancy-specific
Authority: R18–R21; applicable state codes; related K tags
	☐
	☐
	☐
	☐
	


Training exercises and safety testing schedule
	Activity
	Baseline / What to verify
	Evidence

	EP plan / Policies / Communication
	Review/update at least every 2 years; address significant changes and lessons learned.
	Versions, approvals, change log

	EP training
	Initial role-based training; at least every 2 years; changed policies and periodic rehearsal.
	Rosters, content, staff knowledge

	CMS EP exercises
	Twice each year: annual full-scale/qualifying functional plus additional qualifying exercise.
	Calendar, AAR, correction evidence

	Health care fire drills
	Quarterly on each shift under applicable LSC/K712; varied conditions and documented response.
	Shift matrix, evaluation, alarm records

	Maine hospice education
	4-hour orientation before service; 18 hours first-year education including orientation; 8 hours annually thereafter. Apply rule exceptions.
	Ch.120 §§5.F–5.H records

	Generator / EPSS / ATS
	Applicable weekly inspection, monthly load/ATS testing and supplemental/36-month duties; verify category and code.
	K918 schedules, tests, repairs

	Fire protection / Installed systems
	Full component-specific NFPA inspection, testing and maintenance schedules; one annual visit may not cover all duties.
	Inventories, reports, corrections

	Dampers / Installed
	Verify initial and recurring cycles; do not automatically apply the hospital six-year exception to freestanding hospice.
	K521 inventory and adopted interval

	Sprinkler / Alarm impairment
	Sprinkler shutdown >10 hours: evacuation or fire watch under §418.110(d)(5). Apply separate alarm and any earlier AHJ triggers.
	Notifications, watch, restoration



	SUPPORTING POLICIES AND EVIDENCE
Record locations for implementation and survey review


Patient and caregiver emergency planning practices
	ID
	Requirement
	Met
	Partial
	Not
Met
	N/A
	EOP Location / Evidence / Notes

	PL01
	Maintain current patient profiles and facility census: room/location, care team, decision-maker, mobility/cognition, communication needs, medications, oxygen/DME, power dependence and safe receiving destination.
Scope: P
Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders
	☐
	☐
	☐
	☐
	

	PL02
	Give patients/families accessible instructions on contacting staff, fire response, sheltering/evacuation, essential medications/equipment and emergency communication. Confirm understanding and record education.
Scope: P
Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders
	☐
	☐
	☐
	☐
	

	PL03
	Plan staffing access during disrupted roads/weather, staff transport/lodging, safe facility access and violence response. Prioritize clinical staffing and alternate service arrangements during a prolonged disruption.
Scope: P
Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders
	☐
	☐
	☐
	☐
	

	PL04
	Plan continuity of symptom relief, psychosocial/spiritual support and bereavement services; coordinate pharmacy, transport, vendors, funeral services and death certification arrangements.
Scope: P
Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders
	☐
	☐
	☐
	☐
	

	PL05
	Preserve current goals-of-care, decision-maker, advance-directive and applicable Maine EMS Comfort Care/DNR information during relocation. Confirm clinically authorized orders and receiving-provider handoff.
Scope: P
Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders
	☐
	☐
	☐
	☐
	

	PL06
	Address cyberattack/IT downtime, severe weather, flooding, outbreak, supply failure, workplace violence and simultaneous regional service interruption based on the HVA.
Scope: P
Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders
	☐
	☐
	☐
	☐
	


Supporting policy and record index
	Topic
	EOP / Policy / Evidence location

	HVA, service scope, authority and succession
	

	Patient/staff follow-up and uncontacted-person reporting
	

	Primary/alternate communication and emergency information sharing
	

	Receiving/host agreements, care continuity and transfer records
	

	Initial/refresher training, rehearsals, exercise calendars and AARs
	

	Maine license, qualifications, education and quality assurance
	

	Medication continuity, rights, advance directives and bereavement
	

	Facility evacuation, sheltering, patient/employee tracking
	

	Inpatient subsistence, alternate energy, water and waste
	

	Permits/waivers, life safety plans and installed-system records
	

	Fire drills, component maintenance and impairment/fire-watch plans
	



	CORRECTIVE ACTIONS AND REVIEW APPROVAL
Assign owners verify closure and document the review


Corrective action log
	ID / Gap
	Action / Evidence
	Owner
	Due
	Closed

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


Review and approval
	Role
	Name / Signature
	Date

	Hospice administrator
	
	

	EP / Clinical lead
	
	

	Facilities / Office safety lead
	
	

	Governing body / Designee
	
	



	OFFICIAL REFERENCES AND UPDATE WATCH
Source review October 13 2026 provider-specific edition October 14 2026


Use the current eCFR with the CMS survey manuals, adopted Maine rules, codes and facility-specific directions. Maine Chapter 120’s July 2025 Word conversion is not a substantive July 2025 rule amendment. The companion hospice regulations/resources guide includes additional links for both service models.
R01 • 42 CFR §418.113 — Emergency preparedness
Open official source — Hospice EP program, home-based and direct inpatient requirements.
R02 • CMS State Operations Manual — Appendix Z
Open official source — E-tags, survey procedures and interpretive guidance. Rev. 204, April 16, 2021.
R03 • 42 CFR Part 418 — Hospice
Open official source — Current hospice Conditions of Participation and benefit requirements.
R04 • CMS State Operations Manual — Appendix M
Open official source — Hospice survey protocol and clinical guidance. Rev. 222, June 7, 2024; current regulation controls later changes.
R05 • 42 CFR §418.110 — Direct inpatient hospice
Open official source — Staffing, physical environment, NFPA 101/99, patient rooms and inpatient safety.
R06 • 42 CFR §418.108 — Short-term inpatient care
Open official source — Qualified inpatient facilities, written arrangements and hospice responsibilities.
R07 • 42 CFR §418.112 — Hospice in SNF/NF or ICF/IID
Open official source — Agreements, responsibilities, communication and care coordination with host facilities.
R08 • CMS Life Safety Code / Health Care Facilities Code
Open official source — Federal 2012 NFPA 101 and NFPA 99 adoption, survey and waiver information.
R09 • CMS-2786R — Health Care Fire Safety Survey
Open official source — Official health care occupancy K-tag form. July 2018; select other forms for other occupancies.
R10 • CMS State Operations Manual — Appendix I
Open official source — Life Safety Code survey procedures, scope and facility documentation.
R11 • Maine 10-144 CMR Chapter 120 — Hospice licensing
Open official source — Adopted hospice rule. Last amendment in text: April 1, 2000; July 2025 is an accessibility conversion.
R12 • Maine DLC — Rules and regulations
Open official source — Official index linking the adopted hospice rule; confirm later adopted amendments.
R13 • Maine DLC — Medical facilities / Hospice
Open official source — Hospice licensure, Medicare certification and volunteer-only hospice resources. Select Hospice.
R14 • 22 MRS Chapter 1681 — Hospice programs
Open official source — Maine hospice definitions, licensing and other statutory requirements.
R15 • 22 MRS §8624 — Home controlled medications
Open official source — Required home medication management/disposal policy, education and post-death reminder.
R16 • 22 MRS §3477 — Adult protective reporting
Open official source — Mandated reporting of suspected abuse, neglect and exploitation of protected adults.
R17 • Maine DLC — Report a medical facility incident
Open official source — Current facility incident reporting instructions; apply hospice-specific duties and deadlines.
R18 • Maine Fire Marshal — Rules
Open official source — State fire rule chapters, including health care systems, alarms, construction and life safety.
R19 • Maine Fire Marshal — Adopted NFPA standards
Open official source — Posted state editions: NFPA 101 (2018), 99 (2021), 110 (2022) and related standards.
R20 • Maine Fire Marshal — Inspections / Plans review
Open official source — State inspection and plan-review information. Verify facility-specific jurisdiction and requests.
R21 • Maine Fire Marshal — Construction
Open official source — Construction, alteration, occupancy change and permit guidance.
R22 • 25 MRS §2469 — Fuel gas detectors
Open official source — Building and occupancy-specific fuel gas detector duties where applicable.
R23 • Maine Fire Marshal — Proposed rules
Open official source — Monitor proposals separately from adopted rules; no proposed rules listed at review.
R24 • Maine Fire Marshal — Sprinkler shutdown policy
Open official source — Seasonal shutdown provisions concern qualifying unoccupied buildings, not occupied inpatient hospice.
R25 • Maine CDC — Infectious disease reporting
Open official source — Notifiable conditions, reporting tools, Chapter 258 and disease-specific instructions.
R26 • CDC — Core infection prevention practices
Open official source — Clinical guidance for infection prevention across health care settings.
R27 • HHS — HIPAA emergency preparedness
Open official source — Permissible emergency information sharing and privacy planning.
R28 • Maine EMS — Comfort Care / DNR
Open official source — Current Maine EMS forms and program instructions for care goals and resuscitation.
R29 • HCC-ME — Emergency operations planning toolkit
Open planning resource — Planning templates and provider resources; HCC-ME is not a regulatory agency.
R30 • HCC-ME — Training and webinars
Open planning resource — Coalition education and preparedness training.
R31 • ASPR TRACIE
Open planning resource — Health care emergency planning tools and technical assistance.
R32 • Maine DHHS — Rulemaking
Open official source — Proposed and adopted DHHS rules; confirm final text and effective dates.
R33 • Maine Legislature
Open official source — Search bills, amendments, enacted laws and statutory updates.
R34 • CMS — Hospice regulations and notices
Open official source — Final and proposed hospice rules, including FY 2027 changes effective October 1, 2026.
R35 • CMS — Hospices certification hub
Open official source — Certification, survey and current hospice compliance resources.
R36 • CMS — Emergency preparedness rule resources
Open official source — Implementation resources and emergency preparedness survey materials.
R37 • PL 2025 Ch.657 / LD 2224 — Fire standards update
Open official source — Enacted April 13, 2026. Section 3 directs FMO adoption of NFPA 72 (2025); verify implementing rule and effective date.
R38 • LD 2100 — Fuel gas detector bill status
Open official source — Final disposition: died between houses April 7, 2026. Do not apply proposed changes as enacted law.
R39 • MaineCare Section 43 — Hospice rate determination
Open official source — March 31, 2026 draft-rate notice; monitor completed rulemaking and effective rates if MaineCare-enrolled. Separate from EOP duties.
Regulatory change check
PL 2025 Ch.657 §3 directs FMO adoption of NFPA 72 (2025); the FMO standards index listed 2019 at the source review. Verify implementing rule/effective date before determining the alarm code baseline (R19/R37). LD 2100 fuel-gas detector amendments died between houses April 7, 2026 (R38).
The FMO proposed-rules page listed no proposals at the source review. Monitor R23/R32/R33 for later fire, hospice licensing and other applicable changes. Record final legal status, scope and effective dates before implementation. CMS FY 2027 hospice changes effective October 1, 2026 affect certification/election/discharge and payment provisions; current Part 418 controls later changes not yet in older manuals (R03/R34/R35). MaineCare Section 43 draft-rate notices are administrative watch items, separate from EP duties (R39).
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