# INPATIENT HOSPICE
EMERGENCY OPERATIONS PLAN
COMPLIANCE CHECKLIST

CMS Emergency Preparedness • Maine Hospice Requirements
Hospice Operated Inpatient Facilities • Fire and Life Safety

## Organization review information

| Field | Hospice entry |
| --- | --- |
| Hospice / Organization |  |
| Sites / Service area |  |
| Prepared by / Review date |  |
| EOP version / Approval date |  |

For Maine hospices that provide inpatient care directly in their own facilities. Includes shared CMS duties, inpatient emergency policies and exercises, related clinical/state requirements and the 124-category CMS health care fire safety review.

## HCC-ME role

The Healthcare Coalition of Maine (HCC-ME) is not a regulatory agency. This document is a preparedness and planning resource and does not constitute regulatory approval or guarantee compliance. Each hospice remains responsible for applicable federal, state, and local requirements and should consult the appropriate regulatory authorities for official guidance.

Provider-specific edition October 14, 2026 • Source review October 13, 2026
CMS service-model distinctions confirmed October 14, 2026

HOW TO USE THIS CHECKLIST Hospice Operated Inpatient Facility scope and evidence review

Review the EOP, supporting policies, agreements, records, staff knowledge and safety systems. This checklist covers emergency preparedness and related compliance; the complete hospice Conditions of Participation, Maine rules, adopted codes and actual inspection directions govern detailed requirements.

Use this document when the hospice itself operates an inpatient care facility. Providing general inpatient or respite care through a contracted hospital or nursing facility is an arranged-care model governed by §418.108. If the hospice also provides home care, review the separate home-based checklist for those services.

| Step | Action |
| --- | --- |
| 1 | Confirm Maine license, Medicare certification, service model, sites and applicable jurisdiction. |
| 2 | Review each applicable row and record the exact EOP, policy, agreement, training or inspection evidence. |
| 3 | Mark N/A only with a documented basis; apply optional/conditional sections to actual services and installed systems. |
| 4 | Assign owners and due dates, verify corrections and document review approval. |

## Status and authority key

Met = complete and evidenced; Partial = incomplete or unsupported in part; Not Met = absent or deficient; N/A = not applicable with a recorded reason. Review IDs support cross-reference. E-tags/K-tags are CMS identifiers; R numbers identify linked sources. Planning practices are labeled P and are not separate legal mandates.

| Scope | Applies to |
| --- | --- |
| A | All Medicare-certified hospices |
| I | Hospice-operated inpatient facility |
| C | Arranged / contracted inpatient care |
| S | Hospice patients in SNF/NF or ICF/IID |
| M | Maine-licensed hospice |
| P | Planning practice; not a standalone mandate |

| HOSPICE APPLICABILITY PROFILE Confirm services, care settings and responsible parties |  |
| --- | --- |
| Field | Hospice determination / Entry |
| Legal name / Maine license / CCN |  |
| Sites / Service area |  |
| Service model / Certification | Hospice-operated inpatient facility ☐ General inpatient care ☐ Respite ☐ Additional home services ☐ Contracted backup inpatient care ☐ SNF/NF/ICF/IID services |
| Administrator / EP lead / Clinical lead |  |
| EOP version / Approval date |  |
| Patients / Caregiver needs | Mobility, cognition, language, oxygen/DME, electrical dependence, symptom relief and care goals: |
| Receiving / Host facilities / Vendors | Agreements, transport, pharmacy, DME, backup staffing and emergency contacts: |
| Emergency communication | Primary/alternate channels, call lists, reporting officials and downtime records: |
| Facility capacity / Utilities | Beds, census, staffing, transport, shelter supplies, safe care endurance and alternate energy: |
| Buildings / Codes / Permits | Occupancy, new/existing classification, CMS form, approved plans and Maine/local AHJ: |
| Installed protection / Systems | Alarms, sprinklers, medical gases, EPSS/ATS/fuel, dampers, doors, kitchens and emergency shutoffs: |
| Waivers / Equivalencies | Approving authority, written scope, conditions and validity: |
| Review dates | Plan/policy/communication review, training, exercises, applicable drills and inspections: |

## Required CMS exercise cycle

Conduct two exercises each year: an annual community full-scale exercise or qualifying facility functional fallback, plus an additional qualifying exercise. Any documented actual-event exemption replaces only the next required full-scale/functional exercise. Applicable quarterly fire drills are a separate requirement. Authority: §418.113(d)(3); R01/R02.

PART I CMS HOSPICE EMERGENCY PREPAREDNESS Hospice Operated Inpatient Facility requirements under 42 CFR 418.113

## Program, risk assessment and continuity

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP01 | Maintain an implemented EP program complying with applicable federal, state and local requirements; link plan, policies, communication, training and testing. Scope: A Authority: R01/R02; §418.113; E0001 | ☐ | ☐ | ☐ | ☐ |  |
| EP02 | Maintain an emergency plan; document review and updates at least every 2 years and after changes or identified deficiencies. Scope: A Authority: R01/R02; §418.113(a); E0004 | ☐ | ☐ | ☐ | ☐ |  |
| EP03 | Document facility-based and community-based all-hazards risk assessments. Include the service area, office operations, care locations and capabilities. Scope: A Authority: R01/R02; §418.113(a)(1); E0006 | ☐ | ☐ | ☐ | ☐ |  |
| EP04 | Develop strategies for identified emergencies, including power failures, natural disasters and other hazards that could affect hospice services. Scope: A Authority: R01/R02; §418.113(a)(2); E0006 | ☐ | ☐ | ☐ | ☐ |  |
| EP05 | Describe patient population, types of services, ability to continue operations, delegation of authority and succession plans. Scope: A Authority: R01/R02; §418.113(a)(3); E0007 | ☐ | ☐ | ☐ | ☐ |  |
| EP06 | Maintain a process for cooperating and collaborating with local, tribal, regional, state and federal emergency preparedness officials to support an integrated response. Scope: A Authority: R01/R02; §418.113(a)(4); E0009 | ☐ | ☐ | ☐ | ☐ |  |

## Policies, patient follow-up and home evacuation

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP07 | Base policies on the plan, HVA and communication plan; review and update at least every 2 years. Scope: A Authority: R01/R02; §418.113(b); E0013 | ☐ | ☐ | ☐ | ☐ |  |
| EP08 | Follow up with on-duty staff and patients to determine needed services during an emergency. Define contact attempts, escalation and documentation. Scope: A Authority: R01/R02; §418.113(b)(1); E0016 | ☐ | ☐ | ☐ | ☐ |  |
| EP09 | Notify state and local officials of on-duty staff or patients whom the hospice cannot contact; keep accessible reporting contacts and records. Scope: A Authority: R01/R02; §418.113(b)(1); E0016 | ☐ | ☐ | ☐ | ☐ |  |
| EP10 | Notify state and local officials about patients needing evacuation from their homes at any time because of an emergency. Evaluate medical/psychiatric needs and home conditions. Scope: A — residential patients, if applicable Authority: R01/R02; §418.113(b)(2); E0019 | ☐ | ☐ | ☐ | ☐ |  |
| EP11 | Preserve patient documentation, confidentiality and availability during downtime, relocation and emergency service disruption. Scope: A Authority: R01/R02; §418.113(b)(3); E0023 | ☐ | ☐ | ☐ | ☐ |  |
| EP12 | Plan use of hospice employees and surge staff, including integrating state/federally designated health care professionals during an emergency. Scope: A Authority: R01/R02; §418.113(b)(4); E0024 | ☐ | ☐ | ☐ | ☐ |  |
| EP13 | Arrange with other hospices or providers to receive patients when hospice operations are limited or interrupted. Identify care, transport, medication and information responsibilities. Scope: A Authority: R01/R02; §418.113(b)(5); E0025 | ☐ | ☐ | ☐ | ☐ |  |

## Additional requirements for directly operated inpatient hospice

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP14 | Provide shelter in place for patients, hospice employees and volunteers remaining in the facility; define safe locations, staffing and continued care. Scope: I Authority: R01/R02; §418.113(b)(6)(i); E0022 | ☐ | ☐ | ☐ | ☐ |  |
| EP15 | Plan safe evacuation, including care/treatment needs, staff responsibilities, transport, evacuation locations and primary/alternate communication with outside assistance. Scope: I Authority: R01/R02; §418.113(b)(6)(ii); E0020 | ☐ | ☐ | ☐ | ☐ |  |
| EP16 | Provide food, water, medical and pharmaceutical supplies for patients and staff during evacuation or sheltering. Document quantities and replenishment assumptions. Scope: I Authority: R01/R02; §418.113(b)(6)(iii)(A); E0015 | ☐ | ☐ | ☐ | ☐ |  |
| EP17 | Provide alternate energy to maintain safe temperatures, protect food/medications, provide emergency lighting and maintain fire detection, extinguishing and alarm systems. Scope: I Authority: R01/R02; §418.113(b)(6)(iii)(B); E0015 | ☐ | ☐ | ☐ | ☐ |  |
| EP18 | Provide sewage and waste disposal during sheltering or evacuation; address loss of water and sanitation services. Scope: I Authority: R01/R02; §418.113(b)(6)(iii)(C); E0015 | ☐ | ☐ | ☐ | ☐ |  |
| EP19 | Address the hospice role in care at an alternate site under a declared §1135 waiver. Verify actual waiver authority, terms and site arrangements before relying on relief. Scope: I Authority: R01/R02; §418.113(b)(6)(iv); E0026 | ☐ | ☐ | ☐ | ☐ |  |
| EP20 | Track on-duty hospice employees and sheltered patients during the emergency. If relocated, document the receiving facility or other location name and location. Scope: I Authority: R01/R02; §418.113(b)(6)(v); E0018 | ☐ | ☐ | ☐ | ☐ |  |

## Communication, information sharing and assistance

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP21 | Maintain a communication plan complying with federal/state/local law; review and update at least every 2 years. Scope: A Authority: R01/R02/R27; §418.113(c); E0029 | ☐ | ☐ | ☐ | ☐ |  |
| EP22 | Maintain names/contact information for hospice employees, contracted service providers, each patient’s physician and other hospices. Scope: A Authority: R01/R02/R27; §418.113(c)(1); E0030 | ☐ | ☐ | ☐ | ☐ |  |
| EP23 | Maintain contacts for federal, state, tribal, regional and local emergency preparedness staff and other assistance sources. Scope: A Authority: R01/R02/R27; §418.113(c)(2); E0031 | ☐ | ☐ | ☐ | ☐ |  |
| EP24 | Provide primary and alternate ways to communicate with hospice employees and federal/state/tribal/regional/local emergency management agencies. Scope: A Authority: R01/R02/R27; §418.113(c)(3); E0032 | ☐ | ☐ | ☐ | ☐ |  |
| EP25 | Provide a way to share needed medical documentation with other health care providers to maintain continuity of care. Scope: A Authority: R01/R02/R27; §418.113(c)(4); E0033 | ☐ | ☐ | ☐ | ☐ |  |
| EP26 | Provide a way to release patient information during evacuation consistent with 45 CFR §164.510(b)(1)(ii). Scope: A Authority: R01/R02/R27; §418.113(c)(5); E0033 | ☐ | ☐ | ☐ | ☐ |  |
| EP27 | Provide a way to communicate patients’ general condition and location consistent with 45 CFR §164.510(b)(4). Scope: A Authority: R01/R02/R27; §418.113(c)(6); E0033 | ☐ | ☐ | ☐ | ☐ |  |
| EP28 | Provide a way to communicate inpatient occupancy, needs and ability to assist to the AHJ, Incident Command Center or its designee. Scope: I Authority: R01/R02/R27; §418.113(c)(7); E0034 | ☐ | ☐ | ☐ | ☐ |  |

## Training and staff knowledge

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP29 | Maintain a training and testing program based on the plan, HVA, policies and communication plan; review/update at least every 2 years. Scope: A Authority: R01/R02/R03; §418.113(d); E0036 | ☐ | ☐ | ☐ | ☐ |  |
| EP30 | Provide initial EP training consistent with roles to new/existing hospice employees, including volunteers under the employee definition, and persons providing services under arrangement. Scope: A Authority: R01/R02/R03; §418.113(d)(1)(i); §418.3; E0037 | ☐ | ☐ | ☐ | ☐ |  |
| EP31 | Demonstrate staff knowledge of emergency procedures through interview, observation or other documented evidence. Scope: A Authority: R01/R02/R03; §418.113(d)(1)(ii); E0037 | ☐ | ☐ | ☐ | ☐ |  |
| EP32 | Provide EP training at least every 2 years; keep attendance, content, roles and competency evidence. Scope: A Authority: R01/R02/R03; §418.113(d)(1)(iii); E0037 | ☐ | ☐ | ☐ | ☐ |  |
| EP33 | Periodically review and rehearse the emergency plan with hospice staff, including nonemployee staff. Scope: A Authority: R01/R02/R03; §418.113(d)(1)(iv); E0037 | ☐ | ☐ | ☐ | ☐ |  |
| EP34 | Document training and provide training on significantly updated emergency policies and procedures. Scope: A Authority: R01/R02/R03; §418.113(d)(1)(v)–(vi); E0037 | ☐ | ☐ | ☐ | ☐ |  |

## Direct inpatient hospice exercise cycle

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP39 | Test the emergency plan twice per year; keep an annual calendar distinguishing the two required exercises from routine fire drills. Scope: I Authority: R01/R02; §418.113(d)(3); E0039 | ☐ | ☐ | ☐ | ☐ |  |
| EP40 | Annually participate in a community full-scale exercise, or a facility-based functional exercise when a community full-scale exercise is unavailable. Document the fallback basis. Scope: I Authority: R01/R02; §418.113(d)(3)(i); E0039 | ☐ | ☐ | ☐ | ☐ |  |
| EP41 | Conduct an additional annual qualifying community full-scale, facility functional, mock disaster drill or facilitated tabletop/workshop. Scope: I Authority: R01/R02; §418.113(d)(3)(ii); E0039 | ☐ | ☐ | ☐ | ☐ |  |
| EP42 | Document real-event activation and any exemption from the next full-scale/functional exercise. Analyze events and exercises, retain records and update the plan; the additional annual exercise remains required. Scope: I Authority: R01/R02; §418.113(d)(3)(i), (iii); E0039 | ☐ | ☐ | ☐ | ☐ |  |

## Optional integrated health care system program

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| EP43 | If using an integrated program, demonstrate each separately certified facility’s active participation and account for its unique circumstances, patient population and services. Scope: A Authority: R01/R02; §418.113(e)(1)–(2); E0042 | ☐ | ☐ | ☐ | ☐ |  |
| EP44 | Demonstrate the hospice can use and implement the integrated program. Maintain a unified community HVA and each separately certified facility’s individual HVA; the plan satisfies §418.113(a)(2)–(4). Scope: A Authority: R01/R02; §418.113(e)(3)–(4); E0042 | ☐ | ☐ | ☐ | ☐ |  |
| EP45 | Maintain integrated policies/procedures, communication plan and training/testing program meeting the hospice requirements; retain facility-specific implementation evidence. Scope: A Authority: R01/R02; §418.113(e)(5); E0042 | ☐ | ☐ | ☐ | ☐ |  |

PART II CLINICAL CONTINUITY AND MAINE HOSPICE REQUIREMENTS Shared requirements and service-specific obligations

## Hospice clinical continuity and patient protections

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| CP01 | Protect patient rights, grievances, advance directives, safety and freedom from abuse during emergencies. Preserve accessible communication and informed care decisions. Scope: A Authority: R03/R04; §418.52 | ☐ | ☐ | ☐ | ☐ |  |
| CP02 | Maintain timely initial/comprehensive assessments and reassessment, including new symptoms, psychosocial needs, caregiver capacity and emergency vulnerabilities. Scope: A Authority: R03/R04; §418.54 | ☐ | ☐ | ☐ | ☐ |  |
| CP03 | Maintain and revise individualized interdisciplinary plans of care and coordination as needs, setting, staffing or available services change. Scope: A Authority: R03/R04; §418.56 | ☐ | ☐ | ☐ | ☐ |  |
| CP04 | Maintain required 24/7 availability of nursing, physician services and drugs/biologicals; keep other covered services reasonably available as required. Maintain on-call and backup arrangements. Scope: A Authority: R03/R04; §418.100(c); §418.64 | ☐ | ☐ | ☐ | ☐ |  |
| CP05 | Maintain access to required drugs, medical supplies and DME, safe administration/storage, controlled medication procedures, and patient/family education. Arrange backups for critical equipment. Scope: A Authority: R03/R04; §418.106 | ☐ | ☐ | ☐ | ☐ |  |
| CP06 | Maintain a documented infection-control program, surveillance and education for staff, patients and caregivers; apply emergency outbreak procedures. Scope: A Authority: R03/R04; §418.60 | ☐ | ☐ | ☐ | ☐ |  |
| CP07 | Maintain complete, authenticated and confidential clinical records accessible for care. Test downtime documentation and subsequent reconciliation. Scope: A Authority: R03/R04; §418.104(a)–(c) | ☐ | ☐ | ☐ | ☐ |  |
| CP08 | Retain clinical records at least 6 years after death/discharge unless a longer state requirement applies. If operations discontinue, notify the State agency and CMS Regional office about storage and access. Scope: A Authority: R03/R04; §418.104(d) | ☐ | ☐ | ☐ | ☐ |  |
| CP09 | Provide required discharge/transfer summaries and records to the receiving facility or attending physician; include urgent medication and care information. Scope: A Authority: R03/R04; §418.104(e) | ☐ | ☐ | ☐ | ☐ |  |
| CP10 | Maintain lawful discharge and election processes during disruption. Obtain the required written physician discharge order before discharge under §418.26(a); emergency relocation is not automatically revocation or discharge. Scope: A Authority: R03/R04; §418.26; §418.24 | ☐ | ☐ | ☐ | ☐ |  |
| CP11 | Use QAPI to address emergency-related adverse events, service interruptions, infections and corrective actions with governing-body oversight. Scope: A Authority: R03/R04; §418.58 | ☐ | ☐ | ☐ | ☐ |  |
| CP12 | Maintain governance, qualified staffing and service arrangements compliant with federal/state/local requirements. Verify qualifications and assigned emergency responsibilities. Scope: A Authority: R03/R04; §418.100; §418.114; §418.116 | ☐ | ☐ | ☐ | ☐ |  |

## Direct inpatient hospice environment and staffing

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| IP01 | Provide staffing suited to patient volume and acuity, 24-hour nursing services and an RN providing direct care on each shift when any patient receives general inpatient care. Scope: I Authority: R05/R04; §418.110(a)–(b) | ☐ | ☐ | ☐ | ☐ |  |
| IP02 | Maintain a safe environment, sanitation, regulated waste disposal, comfortable temperature/light/ventilation, emergency gas and water supply, and scheduled maintenance of essential emergency equipment. Scope: I Authority: R05/R04; §418.110(c)(1)–(4) | ☐ | ☐ | ☐ | ☐ |  |
| IP03 | Apply federal NFPA 101 (2012) and NFPA 99 (2012), incorporated TIAs and approved waivers. NFPA 99 federal adoption excludes Chapters 7, 8, 12 and 13; state duties remain separate. Scope: I Authority: R05/R04; §418.110(d); §418.110(e) | ☐ | ☐ | ☐ | ☐ |  |
| IP04 | Use positive-latching corridor doors; prohibit roller latches. Assess ABHR placement and safeguards for vulnerable patients. Scope: I Authority: R05/R04; §418.110(d)(1), (4) | ☐ | ☐ | ☐ | ☐ |  |
| IP05 | For a sprinkler shutdown exceeding 10 hours, evacuate the affected building/portion until restored or establish a fire watch. Apply any earlier code/AHJ trigger and document notifications. Scope: I Authority: R05/R04; §418.110(d)(5) | ☐ | ☐ | ☐ | ☐ |  |
| IP06 | Provide required outside windows/doors in sleeping rooms. Apply the 36-inch maximum sill for buildings constructed after July 5, 2016 and any documented permitted exception. Scope: I Authority: R05/R04; §418.110(d)(6); K381 | ☐ | ☐ | ☐ | ☐ |  |
| IP07 | Preserve a home-like atmosphere, privacy, family visiting/overnight arrangements, required room size and occupancy, above-grade rooms and accessible functioning call systems; record authorized waivers. Scope: I Authority: R05/R04; §418.110(f)–(g) | ☐ | ☐ | ☐ | ☐ |  |
| IP08 | Maintain safe toilets/bathing, regulated hot water, infection prevention, sanitation, linens and sanitary dietary services consistent with patient needs. Scope: I Authority: R05/R04; §418.110(h)–(m) | ☐ | ☐ | ☐ | ☐ |  |
| IP09 | Apply patient-rights safeguards, clinical authorization, monitoring and staff training for any restraints or seclusion; do not use them for convenience or routine evacuation control. Scope: I Authority: R05/R04; §418.110(n)–(o) | ☐ | ☐ | ☐ | ☐ |  |
| IP10 | Maintain reporting procedures for deaths associated with restraints/seclusion and the required CMS reporting pathway and timing. Scope: I Authority: R05/R04; §418.110(p) | ☐ | ☐ | ☐ | ☐ |  |

## Arranged inpatient care and hospice in host facilities

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| CO01 | Arrange symptom-management, pain-control and respite care with participating facilities meeting the applicable requirements for that level of care, including nursing and life safety. Scope: C Authority: R06/R07/R01; §418.108(a)–(b) | ☐ | ☐ | ☐ | ☐ |  |
| CO02 | Maintain a written agreement defining hospice oversight, plan of care, record availability, information transmission and hospice orientation of facility personnel. Scope: C Authority: R06/R07/R01; §418.108(c) | ☐ | ☐ | ☐ | ☐ |  |
| CO03 | Maintain a signed hospice/host-facility agreement before service begins; identify patient-care responsibilities, communication, medication responsibilities and notice of relevant changes/events. Scope: S Authority: R06/R07/R01; §418.112(a)–(c) | ☐ | ☐ | ☐ | ☐ |  |
| CO04 | Ensure required immediate abuse/neglect reporting and communication, coordinated care planning and information exchange; retain hospice professional management and designated coordination. Scope: S Authority: R06/R07/R01; §418.112(c)–(e) | ☐ | ☐ | ☐ | ☐ |  |
| CO05 | Coordinate the hospice EOP with host-facility evacuation, sheltering, patient accountability and care continuity. Record which organization maintains building systems and supporting fire-safety records. Scope: C / S / P Authority: R06/R07/R01; §418.108; §418.112; §418.113 | ☐ | ☐ | ☐ | ☐ |  |

## Maine hospice licensing and operational requirements

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ME01 | Maintain a Maine hospice license for the approved services and scope. Non-volunteer hospice applicants must meet Maine Medicare-certification requirements; identify the volunteer-only exception. Scope: M Authority: R11–R17/R25; Ch.120 §2.A; 22 MRS Ch.1681 | ☐ | ☐ | ☐ | ☐ |  |
| ME02 | Maintain required application information and approvals, including municipal zoning/building compliance and occupancy certificate where appropriate; include electrical and fire safety approvals, applicable CLIA and biomedical-waste approvals. Scope: M Authority: R11–R17/R25; Ch.120 §§2.B–2.D | ☐ | ☐ | ☐ | ☐ |  |
| ME03 | Notify DLC of changes in ownership, scope, address/telephone, administration or deeming status as required. Ownership changes require at least 30 days’ advance notice; the license is not transferable. Scope: M Authority: R11–R17/R25; Ch.120 §§2.C, 2.F | ☐ | ☐ | ☐ | ☐ |  |
| ME04 | Track the actual license expiration and renewal requirements; submit renewal at least 20 days before expiration. Confirm current license terms with DLC. Scope: M Authority: R11–R17/R25; Ch.120 §3.C | ☐ | ☐ | ☐ | ☐ |  |
| ME05 | Make records available for inspection; maintain the previous 3 years of relevant licensing/Medicare survey materials. Submit required plans of correction within 10 working days after notification. Scope: M Authority: R11–R17/R25; Ch.120 §3.B | ☐ | ☐ | ☐ | ☐ |  |
| ME06 | Immediately report suspected abuse/neglect/exploitation through required internal and appropriate state pathways. Protect against further harm and maintain investigation/reporting records. Scope: M Authority: R11–R17/R25; Ch.120 §3.B(9); 22 MRS §3477 | ☐ | ☐ | ☐ | ☐ |  |
| ME07 | Review complaints within 2 business days; incorporate findings into quality assurance, investigate timely, and report required investigation results. Scope: M Authority: R11–R17/R25; Ch.120 §3.B(9) | ☐ | ☐ | ☐ | ☐ |  |
| ME08 | Maintain orderly closure and continuity arrangements, organizational authority and staff orientation. Planned closure requires orderly patient-transfer arrangements at least 30 days before closure under the rule; emergency action must protect patients immediately. Scope: M Authority: R11–R17/R25; Ch.120 §§3.E, 4.A | ☐ | ☐ | ☐ | ☐ |  |
| ME09 | Retain business records/contracts/advertising at least 5 years; maintain qualifications, licenses, orientation, education and personnel records for employed and contracted personnel. Use required identification badges or documented exceptions. Scope: M Authority: R11–R17/R25; Ch.120 §§4.B–4.C | ☐ | ☐ | ☐ | ☐ |  |
| ME10 | Conduct quarterly clinical-record review and an annual overall provider quality-assurance review; use results to correct care and preparedness gaps. Scope: M Authority: R11–R17/R25; Ch.120 §4.D | ☐ | ☐ | ☐ | ☐ |  |
| ME11 | Provide an interdisciplinary care plan and 24-hour, 7-day access to required hospice services; maintain nursing supervision and on-call schedules. Maintain required bereavement services. Scope: M Authority: R11–R17/R25; Ch.120 §§5.D–5.E | ☐ | ☐ | ☐ | ☐ |  |
| ME12 | Provide at least 4 hours of orientation before direct hospice service; track required 18 hours of education, including orientation, within the first year. Apply the rule’s limited ≤20-hours-per-year exception correctly; orientation still applies. Scope: M Authority: R11–R17/R25; Ch.120 §§5.F–5.G | ☐ | ☐ | ☐ | ☐ |  |
| ME13 | After the first year, provide at least 8 hours of continuing/in-service education annually based on hire date; keep completion records. These are general hospice education duties, separate from CMS EP training. Scope: M Authority: R11–R17/R25; Ch.120 §5.H | ☐ | ☐ | ☐ | ☐ |  |
| ME14 | Maintain required care, meeting and discharge records. Maine’s 5-year clinical minimum does not shorten the federal 6-year death/discharge retention duty for Medicare-certified hospices. Scope: M Authority: R11–R17/R25; Ch.120 §§5.I–5.J; §418.104 | ☐ | ☐ | ☐ | ☐ |  |
| ME15 | Verify applicable Medicare certification and state eligibility for directly operated inpatient hospice; document any lawful exception with DLC rather than assuming exemption. Scope: M Authority: R11–R17/R25; Ch.120 §5.K; 22 MRS §8631 | ☐ | ☐ | ☐ | ☐ |  |
| ME16 | Maintain written home controlled-medication policy covering agency/caregiver roles, safe use/storage, expected family disposal, safe methods and access to pharmacy medication-disposal kits. Scope: M — services in private homes, if applicable Authority: R11–R17/R25; 22 MRS §8624(1)–(5) | ☐ | ☐ | ☐ | ☐ |  |
| ME17 | Give advance notice of the post-death reminder letter; provide understandable policy education and retain the required signed acknowledgment. Send the family the disposal-reminder letter with safe-disposal information within 30 days after death. Scope: M — services in private homes, if applicable Authority: R11–R17/R25; 22 MRS §8624(6)–(7) | ☐ | ☐ | ☐ | ☐ |  |
| ME18 | Provide required health care power-of-attorney information and maintain patient wishes, advance directives and clinically authorized care goals through relocation and handoff. Scope: M Authority: R11–R17/R25; Ch.120 §2.D(4); §418.52 | ☐ | ☐ | ☐ | ☐ |  |
| ME19 | Identify event-specific incident and notifiable-condition reporting duties, contacts, forms and deadlines. Use current DLC/CDC instructions; do not import hospital-only sentinel-event requirements without checking statutory applicability. Scope: M Authority: R11–R17/R25; 22 MRS Ch.1681; Maine CDC reporting | ☐ | ☐ | ☐ | ☐ |  |

PART III FIRE LIFE SAFETY AND PHYSICAL SYSTEMS CMS Maine Fire Marshal and local code applicability

CMS inpatient hospice uses NFPA 101/99 (2012) with incorporated TIAs and specified exclusions. Maine separately posts NFPA 101 (2018), 99 (2021), 110 (2022) and other standards (R19). PL 2025 Ch.657 §3 directs NFPA 72 (2025) adoption; verify implementing rule/effective date with FMO (R37). Confirm occupancy, system categories and written approvals. State approval does not itself grant a CMS waiver.

## Code applicability, permits and approvals

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| AH01 | Record occupancy, jurisdiction and applicable code/form for every hospice office, inpatient building and mixed occupancy. Do not apply the inpatient K-tag form automatically to home-based service offices or private homes. Scope: M / I Authority: R05/R08/R18; §418.110; occupancy-specific codes | ☐ | ☐ | ☐ | ☐ |  |
| AH02 | Record new/existing classification, construction/alterations, approved plans, sprinkler coverage, barriers, permits and occupancy approvals; obtain required review before changes. Scope: M / I Authority: R18/R21; FMO Ch.3,4,15,17,19,20 | ☐ | ☐ | ☐ | ☐ |  |
| AH03 | Retain written waiver/equivalency scope, conditions, authority and validity. Maine approvals do not themselves grant a federal CMS waiver. Scope: I Authority: R05/R18; §418.110(d)–(e) | ☐ | ☐ | ☐ | ☐ |  |
| AH04 | Determine fuel-gas detector applicability for each building, occupancy and fuel-burning appliance; document installations, testing and any legal exception. Scope: M Authority: R22; 25 MRS §2469 | ☐ | ☐ | ☐ | ☐ |  |
| AH05 | Record NFPA 99 system categories and electrical/power requirements based on risks and care delivered. Identify emergency loads, fuel endurance and alternate utilities; verify required systems with the AHJ. Scope: I Authority: R01/R05/R19; NFPA 99/110 | ☐ | ☐ | ☐ | ☐ |  |

PART III A FULL CMS K TAG REVIEW 124 categories conditional on applicable inpatient health care occupancy

These prompts cover every unique category in CMS-2786R. Use the official form and governing codes for exact dimensions, exceptions, permitted alternatives, component intervals and testing conditions. Record the basis for any system-specific N/A. Verify additional forms for other occupancies and host facilities.

## K-tag review — Construction, interior finishes and exits

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K100 | General Requirements – Other. Review all remaining general LSC provisions, approved equivalencies, and building documentation; record any requirement not captured by another K-tag. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K111 | Building Rehabilitation. Classify rehabilitation work and verify the applicable NFPA 101 Chapter 43 pathway, permits, construction protections, and acceptance records. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K112 | Sprinkler Requirements for Major Rehabilitation. For major rehabilitation, verify required sprinkler coverage and limits of affected areas against approved plans and applicable new-occupancy rules. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K131 | Multiple Occupancies – Sections of Health Care Facilities. Verify health care occupancy classification and permitted mixed uses; confirm the correct chapters apply to each part of the facility. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K132 | Multiple Occupancies – Contiguous Non-Health Care Occupancies. Verify separation or permitted treatment of contiguous non-healthcare occupancies; inspect barriers, openings, and shared egress. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K133 | Multiple Occupancies – Construction Type. Verify construction requirements where multiple occupancies share the building; retain approved construction and separation determinations. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K161 | Building Construction Type and Height. Verify permitted construction type and height for new or existing occupancy; retain building certification and inspect rated structural protection. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K162 | Roofing Systems Involving Combustibles. Verify permitted combustible roofing and supports, including applicable protection, separation, and existing or new provisions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K163 | Interior Nonbearing Wall Construction. Verify nonbearing interior walls and partitions meet applicable construction and fire protection requirements. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K200 | Means of Egress Requirements – Other. Review additional means-of-egress provisions, accessibility, and unusual configurations not otherwise captured. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K211 | Means of Egress – General. Keep required egress continuously usable and unobstructed. Verify arrangement, furnishings, projections, and permitted wheeled equipment conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K221 | Patient Sleeping Room Doors. Verify sleeping-room doors, permitted locking, latching, and emergency opening arrangements do not prevent rapid rescue or relocation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K222 | Egress Doors. Inspect egress door locks and releases, including clinical or security locking, special-needs locking, delayed egress, and access control; test all required release conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K223 | Doors with Self-Closing Devices. Verify required self-closing doors and approved hold-open releases; inspect operation during alarm and power interruption. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K224 | Horizontal-Sliding Doors. Verify any horizontal sliding doors meet permitted use, supervision, opening, and release requirements. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K225 | Stairways and Smokeproof Enclosures. Inspect stairs and smokeproof enclosures for required protection, dimensions, continuity, and door operation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K226 | Horizontal Exits. Verify horizontal exit barriers, openings, refuge capacity, and egress from both sides; align with relocation routes. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K227 | Ramps and Other Exits. Inspect ramps and other exits for compliant construction, slope, guards, and usable discharge. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K231 | Means of Egress Capacity. Verify egress capacity calculations for the actual patient and occupant loads, including surge and relocation assumptions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K232 | Aisle, Corridor or Ramp Width. Measure clear aisle, corridor, and ramp widths; verify permitted obstructions against the applicable occupancy provisions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K233 | Clear Width of Exit and Exit Access Doors. Measure clear exit and exit-access door widths and verify the correct new or existing requirements and exceptions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K241 | Number of Exits – Story and Compartment. Verify the required number and separation of exits for every story and compartment. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K251 | Dead-End Corridors and Common Path of Travel. Measure dead ends and common paths of travel; verify applicable limits, sprinkler conditions, and permitted exceptions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K252 | Number of Exits – Corridors. Verify corridor exit arrangements and access to appropriately separated exits. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K253 | Number of Exits – Patient Sleeping and Non-Sleeping Rooms. Verify exit numbers and arrangements for patient sleeping and nonsleeping rooms, including room size and occupancy conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K254 | Corridor Access. Verify room-to-corridor access, permitted intervening rooms, and clinical arrangements against approved plans. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K255 | Suite Separation, Hazardous Content, and Subdivision. Verify suite boundaries, separation, hazardous contents, and subdivision; confirm approved suite configuration matches use. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K256 | Sleeping Suites. Verify sleeping-suite area, patient supervision, exits, and internal travel distances. Record suite areas on life safety drawings. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K257 | Non-Sleeping Suites. Verify nonsleeping-suite area, exits, internal travel, and any sprinkler or special-protection conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K261 | Travel Distance to Exits. Measure travel distances from rooms and suites to exits using actual routes and the applicable sprinkler conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K271 | Discharge from Exits. Verify exits discharge safely to a public way, with usable walking surfaces, weather maintenance, and compliant intervening spaces. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K281 | Illumination of Means of Egress. Verify normal means-of-egress illumination throughout required routes and discharge areas. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K291 | Emergency Lighting. Inspect and test emergency lighting, batteries, power supply, duration, and records against the applicable code. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K292 | Life Support Means of Egress. For life-support areas, verify required egress and emergency lighting supply; do not rely on an unsupported single route. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K293 | Exit Signage. Verify required exit signs, direction, visibility, illumination, and backup power. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

## K-tag review — Hazardous areas, cooking and flammable materials

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K300 | Protection – Other. Review other fire protection provisions and record unlisted hazards or deficiencies with the controlling citation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K311 | Vertical Openings – Enclosure. Verify enclosure of vertical openings, penetrations, shafts, stairs, and permitted exceptions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K321 | Hazardous Areas – Enclosure. Verify hazardous areas, including storage, soiled linen, waste, fuel, and mechanical areas, have the required separation, doors, or sprinkler protection. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K322 | Laboratories. Verify laboratory hazard classification and required fire protection, flammable-liquid controls, separation, and NFPA 45 conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K323 | Anesthetizing Locations. Verify anesthetizing-area medical gas valves and alarms, essential power, ventilation, temperature and humidity conditions, and applicable equipment instructions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K324 | Cooking Facilities. Inspect cooking protection, exhaust and hood systems, extinguishing equipment, fuel shutoff, and permitted residential cooking arrangements. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K325 | Alcohol Based Hand Rub Dispenser (ABHR). Verify alcohol hand-rub dispenser locations, spacing, capacity, ignition-source clearance, storage, and protection against inappropriate access. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K331 | Interior Wall and Ceiling Finish. Verify interior wall and ceiling finish classifications and testing or product evidence for installed materials. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K332 | Interior Floor Finish. Verify interior floor finish classifications for corridors, exits, and other regulated areas. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

## K-tag review — Fire alarms, sprinklers and extinguishers

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K341 | Fire Alarm System – Installation. Verify alarm installation, required system coverage, power supplies, initiating devices, monitoring, and acceptance documents. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K342 | Fire Alarm System – Initiation. Verify required manual and automatic alarm initiation, device location, accessibility, and alarm transmission. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K343 | Fire Alarm – Notification. Verify occupant and staff notification, required signals, annunciation, and response arrangements. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K344 | Fire Alarm – Control Functions. Test required alarm controls, including door release, HVAC interfaces, smoke control, elevator recall, and other linked systems. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K345 | Fire Alarm System – Testing and Maintenance. Maintain approved fire alarm inspection, testing, and maintenance records, including annual functional testing and applicable device-specific intervals. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K346 | Fire Alarm – Out of Service. For required alarms unavailable over 4 hours in 24 hours, notify the AHJ and evacuate or provide an approved fire watch; record coverage, patrols, restoration, and earlier AHJ conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K347 | Smoke Detection. Verify required smoke detection and sensitivity testing, including alarm-control locations and permitted detection arrangements. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K351 | Sprinkler System – Installation. Verify required sprinkler coverage, system design, permitted exceptions, exterior canopies, obstruction clearance, and spare components. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K352 | Sprinkler System – Supervisory Signals. Verify sprinkler supervisory signals, valve supervision, waterflow detection, and annunciation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K353 | Sprinkler System – Maintenance and Testing. Maintain sprinkler and standpipe inspection, testing, maintenance, deficiency corrections, and records, including relevant quarterly, annual, 3-year, and 5-year tasks. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K354 | Sprinkler System – Out of Service. For sprinkler impairment, determine scope and risks and notify required authorities. Over 10 hours in 24 hours, evacuate the affected area or provide an approved fire watch until restored. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K355 | Portable Fire Extinguishers. Verify appropriate extinguishers, placement, access, inspections, maintenance, and applicable internal service or hydrostatic test records. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K361 | Corridors – Areas Open to Corridor. Verify conditions for areas open to corridors, including permitted waiting, nursing, treatment, and other spaces. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K362 | Corridors – Construction of Walls. Verify corridor wall construction, continuity, rated or permitted nonrated conditions, and penetrations. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K363 | Corridor – Doors. Verify corridor doors close and latch as required, fit openings, resist smoke passage, and have only permitted exceptions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K364 | Corridor – Openings. Verify corridor openings and transfer grilles comply with the applicable limitations and protection. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

## K-tag review — Corridors, smoke barriers and patient rooms

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K371 | Subdivision of Building Spaces – Smoke Compartments. Verify required smoke compartment number, size, arrangement, travel distance, and separation by approved drawings and observation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K372 | Subdivision of Building Spaces – Smoke Barrier Construction. Inspect smoke barrier continuity and penetrations, including concealed spaces, ducts, dampers, and firestop systems. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K373 | Subdivision of Building Spaces – Accumulation Space. Verify sufficient accumulation or refuge space on both sides of smoke barriers for relocated patients and other occupants. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K374 | Subdivision of Building Spaces – Smoke Barrier Doors. Inspect smoke barrier doors, closing and latching where required, glazing, clearance, meeting edges, and permitted configurations. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K379 | Smoke Barrier Door Glazing. Verify glazing in smoke barrier doors has the required ratings or protection and is correctly installed. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K381 | Sleeping Room Outside Windows and Doors. Verify outside sleeping-room windows or doors, with applicable sill height and exceptions; apply hospice §418.110(d)(6), including outside windows/doors and applicable sill-height conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

## K-tag review — Building service systems

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K400 | Special Provisions – Other. Review additional special provisions and identify any Chapter 18 or 19 conditions not otherwise captured. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K421 | High-Rise Buildings. For high-rise buildings, verify required sprinkler, alarm, smoke control, egress, and emergency provisions and their inspection records. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K500 | Building Services – Other. Review remaining building-service requirements and link service failures to utility response procedures. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K511 | Utilities – Gas and Electric. Verify gas and electrical utility installations, shutoffs, labeling, protection, and code compliance. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K521 | HVAC. Verify HVAC installation, shutoffs, fire and smoke dampers, inspections, testing, and maintenance. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K522 | HVAC – Any Heating Device. Verify heating devices meet required installation, location, combustion, and protection conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K523 | HVAC – Suspended Unit Heaters. Inspect suspended unit heaters for permitted locations and protections, including separation from patient and combustible hazards. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K524 | HVAC – Direct-Vent Gas Fireplaces. For direct-vent gas fireplaces, verify permitted locations, barriers, equipment, and safeguards. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K525 | HVAC – Solid Fuel-Burning Fireplaces. For solid-fuel fireplaces, verify separation from sleeping areas, compliant enclosure, heat resistance, and required carbon monoxide detection. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K531 | Elevators. Verify elevator fire service operation, recall, hoistway protection, inspection records, and evacuation restrictions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K532 | Escalators, Dumbwaiters, and Moving Walks. Verify protection and permitted use of escalators, dumbwaiters, and moving walks, including opening enclosures. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K541 | Rubbish Chutes, Incinerators, and Laundry Chutes. Verify chute, incinerator, and laundry-shaft protection, discharge rooms, sprinklers, and door operation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

## K-tag review — Operating features and emergency procedures

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K700 | Operating Features – Other. Review additional operating features and staffing practices not covered by another K-tag. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K711 | Evacuation and Relocation Plan. Maintain a written fire protection, relocation, and evacuation plan with prompt reporting, alarm activation, containment, extinguishment, rescue, staff duties, and fire-department cooperation; verify accessibility and staff instruction. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K712 | Fire Drills. Conduct fire drills at least quarterly on each shift, at varied expected and unexpected times, with alarm transmission and simulated fire conditions. Retain shift, scenario, response, and improvement records. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K741 | Smoking Regulations. Maintain smoking restrictions, supervision where needed, ash disposal, signs, and permitted metal containers; verify ignition-risk controls. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K751 | Draperies, Curtains, and Loosely Hanging Fabrics. Verify flame-resistance evidence and permitted use of drapes, curtains, and hanging fabrics. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K752 | Upholstered Furniture and Mattresses. Verify applicable testing, product evidence, and protection for upholstered furniture and mattresses. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K753 | Combustible Decorations. Verify decoration combustibility, limits, locations, and documentation of allowed materials. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K761 | Maintenance, Inspection & Testing - Doors. Inspect and test required fire door assemblies annually using qualified personnel and written records. Routinely inspect other corridor and smoke barrier doors; do not automatically treat every door as an annual NFPA 80 fire door. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K754 | Soiled Linen and Trash Containers. Verify linen and trash container capacity, density, hazardous-area storage, and applicable recycling exceptions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K771 | Engineer Smoke Control Systems. For engineered smoke control, maintain operational testing, maintenance, trained staff, and system documentation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K781 | Portable Space Heaters. Verify restrictions on portable space heaters and any permitted use, including element temperature and approved location. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K791 | Construction, Repair, and Improvement Operations. Maintain construction, repair, and renovation safeguards, temporary egress, fire protection, hot-work controls, and NFPA 241 protections. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

## K-tag review — Health care facility systems and equipment

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K900 | Health Care Facilities Code - Other. Review other applicable NFPA 99 requirements. Record federal exclusions of Chapters 7, 8, 12, and 13 separately from Maine obligations. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K901 | Fundamentals – Building System Categories. Maintain formal, documented risk assessments assigning building-system Categories 1 through 4; qualified personnel determine the risk of system failure. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K902 | Gas and Vacuum Piped Systems – Other. Review remaining medical gas and vacuum Chapter 5 provisions not addressed by specific tags. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K903 | Gas and Vacuum Piped Systems – Categories. Verify medical gas, vacuum, WAGD, and air system categories match clinical risk and permitted sedation or anesthesia use. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K904 | Gas and Vacuum Piped Systems – Warning Systems. Verify required medical gas and vacuum master, area, and local warning systems and staff response to abnormal conditions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K905 | Gas and Vacuum Piped Systems – Central Supply System. Verify central supply design, source equipment, reserve supply, access, separation, and protection. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K906 | Gas and Vacuum Piped Systems – Central Supply System Operations. Verify safe central supply operations and continuity under source failure, maintenance, and reserve depletion. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K907 | Gas and Vacuum Piped Systems – Maintenance Program. Maintain medical gas and vacuum maintenance policies, equipment inventories, schedules, qualified personnel, and service records. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K908 | Gas and Vacuum Piped Systems – Inspection and Testing Operations. Verify inspection and testing of medical gas and vacuum components, alarms, safety devices, and corrective actions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K909 | Gas and Vacuum Piped Systems – Information and Warning Signs. Verify medical gas and vacuum warning signs, instructions, and required information at sources, valves, and outlets. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K910 | Gas and Vacuum Piped Systems – Modifications. For medical gas modifications, retain permits, qualified installer and verifier records, testing, and acceptance before clinical use. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K911 | Electrical Systems – Other. Review remaining electrical system Chapter 6 provisions, protections, and required electrical system documentation. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K912 | Electrical Systems – Receptacles. Verify correct receptacle type, location, grounding, and identification at patient beds and anesthetizing locations. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K913 | Electrical Systems – Wet Procedure Locations. Maintain wet-procedure location risk determinations and required isolated power or ground-fault protection, including tests. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K914 | Electrical Systems – Maintenance and Testing. Test receptacles after installation or repair and at applicable intervals. Nonhospital-grade patient-bed and anesthetizing-location receptacles require intervals not exceeding 12 months; document hospital-grade schedules. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K915 | Electrical Systems – Essential Electric System Categories. Verify essential electric system type and branches match clinical use, life-support needs, and formal risk categorization. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K916 | Electrical Systems – Essential Electric System Alarm Annunciator. Verify essential-power alarm annunciation, monitoring location, staffed response, and system testing. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K917 | Electrical Systems – Essential Electric System Receptacles. Distinctively mark receptacles or cover plates supplied from life safety and critical branches; verify patient-care staff can identify them. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K918 | Essential electrical system maintenance and testing. Verify life safety and critical branch power within 10 seconds; annually confirm when monthly tests do not demonstrate it. Record weekly generator inspections, 30-minute load tests 12 times annually at 20–40-day intervals, applicable 36-month 4-hour and supplemental load tests, transfer-switch tests, annual main/feeder breaker inspections, NFPA 111 stored-energy tests, and circuit identification. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K919 | Electrical Equipment – Other. Review other electrical equipment Chapter 10 requirements and electrical safety controls. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K920 | Electrical Equipment – Power Cords and Extension Cords. Inspect power strips, special-purpose relocatable power taps, extension cords, and power cords for listing, permitted use, rating, grounding, damage, and prohibited daisy chaining. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K921 | Electrical Equipment – Testing and Maintenance Requirements. Maintain electrical equipment inspections and tests, inventories, qualified staff, records, and safe removal of defective equipment. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K922 | Gas Equipment – Other. Review remaining gas equipment Chapter 11 provisions, safe handling, and emergency response. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K923 | Gas Equipment – Cylinder and Container Storage. Verify medical gas cylinder quantities, secure storage, separation, ventilation, signs, ignition precautions, and empty versus full identification. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K924 | Gas Equipment – Testing and Maintenance Requirements. Inspect and maintain gas equipment according to the required program and manufacturer guidance; retain records and qualified-service evidence. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K925 | Gas Equipment – Respiratory Therapy Sources of Ignition. Control ignition sources where respiratory therapy and oxygen equipment are used. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K926 | Gas Equipment – Qualifications and Training of Personnel. Verify qualifications and training of staff handling gas equipment and emergency shutoffs. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K927 | Gas Equipment – Transfilling Cylinders. Where cylinders are transfilled, verify approved room, ventilation, equipment, signage, separation, and qualified personnel. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K928 | Gas Equipment – Labeling Equipment and Cylinders. Verify required equipment and cylinder labeling, identification, and legibility. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K929 | Oxygen cylinder handling precautions. Verify safe cylinder handling, transport, securement, connections, valve practices, and oxygen precautions. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K930 | Gas Equipment – Liquid Oxygen Equipment. For liquid oxygen, verify installation, transfer and storage safeguards, trained staff, and emergency procedures. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K931 | Hyperbaric Facilities. If hyperbaric services are offered, verify applicable NFPA 99 Chapter 14 safeguards, operation, training, and emergency measures. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K932 | Features of Fire Protection – Other. Review remaining NFPA 99 fire protection provisions not otherwise captured. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |
| K933 | Features of Fire Protection – Fire Loss Prevention in Operating Rooms. Maintain operating-room fire prevention, staff training, ignition and oxygen controls, fire-response procedures, and required periodic reviews and evaluations. Scope: I — if applicable Authority: R05/R08/R09; CMS-2786R; applicable NFPA provisions | ☐ | ☐ | ☐ | ☐ |  |

PART III B FIRE MARSHAL EVIDENCE PACKET Confirm facility-specific inspection requests and adopted codes

Maintain current plans, inventories, testing/maintenance reports, staff fire response and correction records. Apply each documentation category to actual systems and occupancy; retain the current Fire Marshal/local AHJ inspection request with this packet.

## Fire Marshal documentation and inspection evidence

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| FM01 | Life safety drawings show exits, 1-hour and 2-hour barriers, horizontal exits, smoke barriers and compartments, suites, and travel distances. Verify current as-built accuracy. Cross reference K161; K226; K255–257; K261; K371–374. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM02 | Sprinkler reports cover applicable quarterly, 3-year, and 5-year tasks and other required NFPA 25 component intervals. Retain repairs, acceptance, and system design records. Cross reference K351–354. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM03 | Annual fire alarm functional reports and all other applicable device inspection and test intervals; record component inventory, deficiencies, and closure. Cross reference K341–346. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM04 | Smoke detector sensitivity testing at the required intervals and accepted method; identify device locations and due dates. Cross reference K347; NFPA 72. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM05 | Fire damper inventory, access, initial and recurring inspection/test reports. Determine the governing cycle for hospice occupancy; do not assume the hospital six-year exception applies. Cross reference K521; NFPA 80. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM06 | Smoke damper inventory, access, initial and recurring inspection/test reports. Document the applicable code cycle and any approved hospital exception. Cross reference K521; NFPA 105. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM07 | Medical gas component inventories, acceptance/verification, alarm tests, required maintenance and repairs. Retain annual inspection reports if required by the AHJ or system schedule. Cross reference K903–910. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM08 | Annual required fire-door inspection and testing records; inspector qualification or training evidence; repair closure; routine other-door inspection. Cross reference K761. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM09 | Generator/EPSS weekly inspections, monthly load tests, ATS tests, fuel, repairs and applicable supplemental/36-month test records. Determine applicability from system category and code. Cross reference K918 and §418.113(b)(6). Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM10 | Nonhospital-grade patient-bed receptacle tests at intervals no greater than 12 months; identify applicable anesthetizing locations and documented schedules for other receptacles. Cross reference K914. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM11 | Smoking policy and safe ash-disposal or self-closing metal-container arrangements where smoking is allowed; observe implementation. Cross reference K741. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM12 | Quarterly fire drill records for each shift, varied conditions, alarm transmission, evaluations, and corrective actions. Cross reference K712. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM13 | Kitchen hood, exhaust, and suppression inspection and service reports at system-specific intervals; include cleaning and fuel shutoff. Cross reference K324; NFPA 96. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM14 | Portable extinguisher inspections, annual maintenance, and applicable internal-service and hydrostatic test records. Cross reference K355; NFPA 10. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM15 | If hyperbaric services are present, maintain system, operational, training, and emergency evidence for the applicable code. Cross reference K931. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM16 | Complete hospice EP evidence: HVA, plan, policies, communications, patient and on-duty staff follow-up, applicable inpatient power/subsistence, training, exercises, agreements and corrections. Cross reference EP01–EP45. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM17 | Verify required detection protecting fire alarm equipment or control locations; retain detector locations and the approved system design. Cross reference K341; K347. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM18 | Walkways and exit discharge are flat, usable, maintained, and continuous to the public way; inspect holes, ice, and obstructions. Cross reference K271. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM19 | Evaluate exterior overhangs and canopies, including those wider than 4 feet, for required sprinkler coverage and permitted construction or protection exceptions. Cross reference K351; NFPA 13. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM20 | Sleeping and nonsleeping suite areas, dimensions, boundaries, exits, and use are identified and verified on current floor plans. Cross reference K255–257. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |
| FM21 | Smoke compartment number, location, square footage, travel distances, and refuge capacity are shown on plans and verified onsite. Cross reference K371–374. Scope: I / M — system or occupancy-specific Authority: R18–R21; applicable state codes; related K tags | ☐ | ☐ | ☐ | ☐ |  |

## Training exercises and safety testing schedule

| Activity | Baseline / What to verify | Evidence |
| --- | --- | --- |
| EP plan / Policies / Communication | Review/update at least every 2 years; address significant changes and lessons learned. | Versions, approvals, change log |
| EP training | Initial role-based training; at least every 2 years; changed policies and periodic rehearsal. | Rosters, content, staff knowledge |
| CMS EP exercises | Twice each year: annual full-scale/qualifying functional plus additional qualifying exercise. | Calendar, AAR, correction evidence |
| Health care fire drills | Quarterly on each shift under applicable LSC/K712; varied conditions and documented response. | Shift matrix, evaluation, alarm records |
| Maine hospice education | 4-hour orientation before service; 18 hours first-year education including orientation; 8 hours annually thereafter. Apply rule exceptions. | Ch.120 §§5.F–5.H records |
| Generator / EPSS / ATS | Applicable weekly inspection, monthly load/ATS testing and supplemental/36-month duties; verify category and code. | K918 schedules, tests, repairs |
| Fire protection / Installed systems | Full component-specific NFPA inspection, testing and maintenance schedules; one annual visit may not cover all duties. | Inventories, reports, corrections |
| Dampers / Installed | Verify initial and recurring cycles; do not automatically apply the hospital six-year exception to freestanding hospice. | K521 inventory and adopted interval |
| Sprinkler / Alarm impairment | Sprinkler shutdown >10 hours: evacuation or fire watch under §418.110(d)(5). Apply separate alarm and any earlier AHJ triggers. | Notifications, watch, restoration |

SUPPORTING POLICIES AND EVIDENCE Record locations for implementation and survey review

## Patient and caregiver emergency planning practices

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| PL01 | Maintain current patient profiles and facility census: room/location, care team, decision-maker, mobility/cognition, communication needs, medications, oxygen/DME, power dependence and safe receiving destination. Scope: P Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders | ☐ | ☐ | ☐ | ☐ |  |
| PL02 | Give patients/families accessible instructions on contacting staff, fire response, sheltering/evacuation, essential medications/equipment and emergency communication. Confirm understanding and record education. Scope: P Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders | ☐ | ☐ | ☐ | ☐ |  |
| PL03 | Plan staffing access during disrupted roads/weather, staff transport/lodging, safe facility access and violence response. Prioritize clinical staffing and alternate service arrangements during a prolonged disruption. Scope: P Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders | ☐ | ☐ | ☐ | ☐ |  |
| PL04 | Plan continuity of symptom relief, psychosocial/spiritual support and bereavement services; coordinate pharmacy, transport, vendors, funeral services and death certification arrangements. Scope: P Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders | ☐ | ☐ | ☐ | ☐ |  |
| PL05 | Preserve current goals-of-care, decision-maker, advance-directive and applicable Maine EMS Comfort Care/DNR information during relocation. Confirm clinically authorized orders and receiving-provider handoff. Scope: P Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders | ☐ | ☐ | ☐ | ☐ |  |
| PL06 | Address cyberattack/IT downtime, severe weather, flooding, outbreak, supply failure, workplace violence and simultaneous regional service interruption based on the HVA. Scope: P Authority: Implementation aid for R01/R03/R11/R28; validate patient-specific orders | ☐ | ☐ | ☐ | ☐ |  |

## Supporting policy and record index

| Topic | EOP / Policy / Evidence location |
| --- | --- |
| HVA, service scope, authority and succession |  |
| Patient/staff follow-up and uncontacted-person reporting |  |
| Primary/alternate communication and emergency information sharing |  |
| Receiving/host agreements, care continuity and transfer records |  |
| Initial/refresher training, rehearsals, exercise calendars and AARs |  |
| Maine license, qualifications, education and quality assurance |  |
| Medication continuity, rights, advance directives and bereavement |  |
| Facility evacuation, sheltering, patient/employee tracking |  |
| Inpatient subsistence, alternate energy, water and waste |  |
| Permits/waivers, life safety plans and installed-system records |  |
| Fire drills, component maintenance and impairment/fire-watch plans |  |

CORRECTIVE ACTIONS AND REVIEW APPROVAL Assign owners verify closure and document the review

## Corrective action log

| ID / Gap | Action / Evidence | Owner | Due | Closed |
| --- | --- | --- | --- | --- |

## Review and approval

| Role | Name / Signature | Date |
| --- | --- | --- |
| Hospice administrator |  |  |
| EP / Clinical lead |  |  |
| Facilities / Office safety lead |  |  |
| Governing body / Designee |  |  |

OFFICIAL REFERENCES AND UPDATE WATCH Source review October 13 2026 provider-specific edition October 14 2026

Use the current eCFR with the CMS survey manuals, adopted Maine rules, codes and facility-specific directions. Maine Chapter 120’s July 2025 Word conversion is not a substantive July 2025 rule amendment. The companion hospice regulations/resources guide includes additional links for both service models.

R01 • 42 CFR §418.113 — Emergency preparedness
Open official source — Hospice EP program, home-based and direct inpatient requirements.

R02 • CMS State Operations Manual — Appendix Z
Open official source — E-tags, survey procedures and interpretive guidance. Rev. 204, April 16, 2021.

R03 • 42 CFR Part 418 — Hospice
Open official source — Current hospice Conditions of Participation and benefit requirements.

R04 • CMS State Operations Manual — Appendix M
Open official source — Hospice survey protocol and clinical guidance. Rev. 222, June 7, 2024; current regulation controls later changes.

R05 • 42 CFR §418.110 — Direct inpatient hospice
Open official source — Staffing, physical environment, NFPA 101/99, patient rooms and inpatient safety.

R06 • 42 CFR §418.108 — Short-term inpatient care
Open official source — Qualified inpatient facilities, written arrangements and hospice responsibilities.

R07 • 42 CFR §418.112 — Hospice in SNF/NF or ICF/IID
Open official source — Agreements, responsibilities, communication and care coordination with host facilities.

R08 • CMS Life Safety Code / Health Care Facilities Code
Open official source — Federal 2012 NFPA 101 and NFPA 99 adoption, survey and waiver information.

R09 • CMS-2786R — Health Care Fire Safety Survey
Open official source — Official health care occupancy K-tag form. July 2018; select other forms for other occupancies.

R10 • CMS State Operations Manual — Appendix I
Open official source — Life Safety Code survey procedures, scope and facility documentation.

R11 • Maine 10-144 CMR Chapter 120 — Hospice licensing
Open official source — Adopted hospice rule. Last amendment in text: April 1, 2000; July 2025 is an accessibility conversion.

R12 • Maine DLC — Rules and regulations
Open official source — Official index linking the adopted hospice rule; confirm later adopted amendments.

R13 • Maine DLC — Medical facilities / Hospice
Open official source — Hospice licensure, Medicare certification and volunteer-only hospice resources. Select Hospice.

R14 • 22 MRS Chapter 1681 — Hospice programs
Open official source — Maine hospice definitions, licensing and other statutory requirements.

R15 • 22 MRS §8624 — Home controlled medications
Open official source — Required home medication management/disposal policy, education and post-death reminder.

R16 • 22 MRS §3477 — Adult protective reporting
Open official source — Mandated reporting of suspected abuse, neglect and exploitation of protected adults.

R17 • Maine DLC — Report a medical facility incident
Open official source — Current facility incident reporting instructions; apply hospice-specific duties and deadlines.

R18 • Maine Fire Marshal — Rules
Open official source — State fire rule chapters, including health care systems, alarms, construction and life safety.

R19 • Maine Fire Marshal — Adopted NFPA standards
Open official source — Posted state editions: NFPA 101 (2018), 99 (2021), 110 (2022) and related standards.

R20 • Maine Fire Marshal — Inspections / Plans review
Open official source — State inspection and plan-review information. Verify facility-specific jurisdiction and requests.

R21 • Maine Fire Marshal — Construction
Open official source — Construction, alteration, occupancy change and permit guidance.

R22 • 25 MRS §2469 — Fuel gas detectors
Open official source — Building and occupancy-specific fuel gas detector duties where applicable.

R23 • Maine Fire Marshal — Proposed rules
Open official source — Monitor proposals separately from adopted rules; no proposed rules listed at review.

R24 • Maine Fire Marshal — Sprinkler shutdown policy
Open official source — Seasonal shutdown provisions concern qualifying unoccupied buildings, not occupied inpatient hospice.

R25 • Maine CDC — Infectious disease reporting
Open official source — Notifiable conditions, reporting tools, Chapter 258 and disease-specific instructions.

R26 • CDC — Core infection prevention practices
Open official source — Clinical guidance for infection prevention across health care settings.

R27 • HHS — HIPAA emergency preparedness
Open official source — Permissible emergency information sharing and privacy planning.

R28 • Maine EMS — Comfort Care / DNR
Open official source — Current Maine EMS forms and program instructions for care goals and resuscitation.

R29 • HCC-ME — Emergency operations planning toolkit
Open planning resource — Planning templates and provider resources; HCC-ME is not a regulatory agency.

R30 • HCC-ME — Training and webinars
Open planning resource — Coalition education and preparedness training.

R31 • ASPR TRACIE
Open planning resource — Health care emergency planning tools and technical assistance.

R32 • Maine DHHS — Rulemaking
Open official source — Proposed and adopted DHHS rules; confirm final text and effective dates.

R33 • Maine Legislature
Open official source — Search bills, amendments, enacted laws and statutory updates.

R34 • CMS — Hospice regulations and notices
Open official source — Final and proposed hospice rules, including FY 2027 changes effective October 1, 2026.

R35 • CMS — Hospices certification hub
Open official source — Certification, survey and current hospice compliance resources.

R36 • CMS — Emergency preparedness rule resources
Open official source — Implementation resources and emergency preparedness survey materials.

R37 • PL 2025 Ch.657 / LD 2224 — Fire standards update
Open official source — Enacted April 13, 2026. Section 3 directs FMO adoption of NFPA 72 (2025); verify implementing rule and effective date.

R38 • LD 2100 — Fuel gas detector bill status
Open official source — Final disposition: died between houses April 7, 2026. Do not apply proposed changes as enacted law.

R39 • MaineCare Section 43 — Hospice rate determination
Open official source — March 31, 2026 draft-rate notice; monitor completed rulemaking and effective rates if MaineCare-enrolled. Separate from EOP duties.

## Regulatory change check

PL 2025 Ch.657 §3 directs FMO adoption of NFPA 72 (2025); the FMO standards index listed 2019 at the source review. Verify implementing rule/effective date before determining the alarm code baseline (R19/R37). LD 2100 fuel-gas detector amendments died between houses April 7, 2026 (R38).

The FMO proposed-rules page listed no proposals at the source review. Monitor R23/R32/R33 for later fire, hospice licensing and other applicable changes. Record final legal status, scope and effective dates before implementation. CMS FY 2027 hospice changes effective October 1, 2026 affect certification/election/discharge and payment provisions; current Part 418 controls later changes not yet in older manuals (R03/R34/R35). MaineCare Section 43 draft-rate notices are administrative watch items, separate from EP duties (R39).

| Change / Authority | Status / Effective date | Applicable sites / Action / Owner |
| --- | --- | --- |