# LONG-TERM CARE / SKILLED NURSING FACILITY
EMERGENCY OPERATIONS PLAN
COMPLIANCE CHECKLIST

CMS Emergency Preparedness  •  Maine Requirements  •  Fire & Life Safety EOP Readiness  •  LTC/SNF-Specific

| Facility / Organization |  |
| --- | --- |
| Provider Type | Long-Term Care / Skilled Nursing Facility |
| Prepared By |  |
| Review Date |  |

Designed for Maine long-term care and skilled nursing facilities. This checklist integrates CMS emergency preparedness requirements, Maine 10-144 CMR Ch. 110 requirements, and an EOP-focused fire/life-safety readiness crosswalk for LTC/SNF use.

Version: September 14, 2026

HOW TO USE THIS CHECKLIST A survey-readiness and plan-development crosswalk for Maine long-term care / skilled nursing facilities

|  | Important regulatory note This document is a readiness tool, not an official CMS, Maine Division of Licensing and Certification (DLC), Maine Office of State Fire Marshal (FMO), or accreditation survey form. Provider-specific regulations and the current law/code edition control if they differ from this checklist. |
| --- | --- |

## Purpose

Use this checklist to verify that a Long-Term Care / Skilled Nursing Facility Emergency Operations Plan (EOP) and supporting emergency preparedness program contain the applicable CMS elements, Maine long-term care licensing provisions, and fire/life-safety readiness elements. This document is a readiness and documentation crosswalk, not an official CMS, Maine Division of Licensing and Certification (DLC), Maine Office of State Fire Marshal (FMO), local authority having jurisdiction (AHJ), or accreditation survey form. Current provider-specific law, regulation, code, and survey guidance control if they differ from this checklist.

## Recommended workflow

| Step | Action | What to do |
| --- | --- | --- |
| 1 | Identify applicability | Complete the facility profile and confirm LTC/SNF applicability, certification/licensure, accreditation, and fire/life-safety survey layers. |
| 2 | Complete universal review | Work through Part I and document the EOP section, policy, attachment, or other evidence supporting each LTC/SNF requirement. |
| 3 | Complete overlays | Complete Part II-A (CMS Life Safety Code / K-tag readiness), Part II-B (Maine State Fire Marshal / local AHJ overlay), then complete the LTC/SNF-specific requirements in Part III. |
| 4 | Close gaps | Use the corrective-action log to assign owners, due dates, plan revisions, training, and retesting. |

## Identifier key

| Identifier | Meaning |
| --- | --- |
| CMS-EP E-#### | CMS Appendix Z emergency preparedness survey tag. |
| 42 CFR §... | Current federal regulatory citation for the provider type. |
| CMS-LSC K### | Federal CMS Life Safety Code / Form CMS-2786 survey tag (K-tag); not a Maine FMO identifier. |
| ME-FMO | Maine Office of State Fire Marshal rule, State-adopted NFPA standard, inspection, permit, or local-AHJ overlay. |
| ME-DLC Ch. ### | Maine DHHS Division of Licensing and Certification requirement, including 10-144 CMR Ch. 110. |
| HCC-ME REC | Recommended practice included for operational readiness; not labeled as a stand-alone CMS requirement. |
| IF APPLICABLE | Depends on provider type, occupancy, services, facility configuration, or certification status. |
| CROSS-REG | Cross-regulatory verification item spanning Federal, Maine, and/or local requirements; not a stand-alone survey tag. |

## Current code and rule edition note

Verified September 14, 2026 against the Maine Office of State Fire Marshal rules and State-Adopted NFPA Standards: NFPA 1 (2018), NFPA 10 (2018), NFPA 13/13D/13R (2016), NFPA 14 (2013), NFPA 20 (2013), NFPA 25 (2014), NFPA 72 (2019), NFPA 80 (2019), NFPA 96 (2021), NFPA 99 (2021), NFPA 101 (2018), NFPA 110 (2022), and NFPA 241 (2019) are among the State-adopted standards relevant to healthcare and fire/life safety. Maine FMO rules organize these standards principally under Chapters 3, 4, 5, 15, 17, 19, and 20. CMS Form 2786R and 42 CFR §483.73(g) use federally incorporated NFPA editions, including NFPA 99 (2012), NFPA 101 (2012), and NFPA 110 (2010). Facilities must evaluate both federal CMS requirements and current Maine/local AHJ requirements.

## Checklist status definitions

| Status | Use when |
| --- | --- |
| Met | Requirement is fully addressed and supporting evidence can be produced. |
| Partial | Requirement is addressed but incomplete, outdated, inconsistent, or lacking evidence. |
| Not Met | Required element is absent or materially deficient. |
| N/A | Requirement does not apply; document the basis for the N/A determination. |

FACILITY APPLICABILITY PROFILE Complete before using the compliance tables

| Field | Facility Entry |
| --- | --- |
| Facility / Organization |  |
| Physical Address |  |
| CMS Certification Number (if applicable) |  |
| Maine License Number (if applicable) |  |
| Emergency Preparedness Lead |  |
| Executive / Administrator |  |
| Safety / Facilities Lead |  |
| Clinical Lead |  |
| Date of Review |  |
| Next Scheduled Review |  |

## Provider type

| Provider Type | Sector Checklist |
| --- | --- |
| ☒ Long-Term Care / Skilled Nursing Facility | This checklist is specific to this provider type. |

## Regulatory / accreditation profile

Accreditation applicability note: The attached 2024 Joint Commission Emergency Management reference guide addresses Ambulatory Health Care, Ambulatory Surgical Care, Diagnostic Imaging, and Telehealth. It is not used in this checklist as an LTC/SNF accreditation authority. Facilities with accreditation should verify the standards for their actual accreditation program.

| Select | Select |
| --- | --- |
| ☐ Medicare certified | ☐ Medicaid certified |
| ☐ Maine licensed | ☐ Maine FMO inspection applies |
| ☐ CMS Life Safety Code survey applies | ☐ Joint Commission accredited |
| ☐ DNV accredited | ☐ AAAHC accredited |
| ☐ Other accreditation: __________________ |  |

## Applicable fire / life-safety layer

| Selection | Selection / Notes |
| --- | --- |
| ☐ CMS-2786R - Health Care Occupancy | ☐ CMS-2786U - Ambulatory Health Care Occupancy |
| ☐ Other CMS-2786 form: __________________ | ☐ Maine FMO / local AHJ requirements |
| ☐ CMS LSC survey not applicable | Basis / notes: ___________________________ |

PART I — LONG-TERM CARE / SKILLED NURSING FACILITY CMS EMERGENCY PREPAREDNESS CHECKLIST Core CMS emergency preparedness requirements applicable to this provider type

## 1. Emergency Preparedness Program Administration

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0001 | A written emergency preparedness program is established and maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0001 | The organization complies with applicable Federal, State, and local emergency preparedness requirements. | ☐ | ☐ | ☐ | ☐ |  |
| E-0004 | The emergency preparedness program contains a written emergency plan. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 | The program contains emergency preparedness policies and procedures. | ☐ | ☐ | ☐ | ☐ |  |
| E-0029 | The program contains a written emergency communication plan. | ☐ | ☐ | ☐ | ☐ |  |
| E-0036 | The program contains a documented training and testing program. | ☐ | ☐ | ☐ | ☐ |  |
| E-0001 | Emergency preparedness documentation can be produced in writing/electronically for survey review. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | An emergency preparedness lead/coordinator and backup are identified. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | The EOP clearly identifies the organization, locations, and services covered. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Document control includes version, approval/review date, and revision history. | ☐ | ☐ | ☐ | ☐ |  |
| E-0004 | The LTC emergency plan is reviewed and updated at least annually. | ☐ | ☐ | ☐ | ☐ |  |
| E-0001 / HCC-ME REC | Material regulatory, operational, facility, population, or hazard changes are evaluated promptly and incorporated into the emergency preparedness program when needed rather than waiting for the next annual review. | ☐ | ☐ | ☐ | ☐ |  |

## 2. Risk Assessment / Hazard Vulnerability Analysis

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0006 | A documented facility-based risk assessment has been completed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | A documented community-based risk assessment is incorporated or used to inform the plan. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | The risk assessment uses an all-hazards approach. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | The assessment considers hazards likely in the facility’s geographic area. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | The assessment considers vulnerabilities created by the facility’s location, infrastructure, and operations. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006/E-0007 | The assessment considers the patient/resident/client population and its vulnerabilities. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Strategies are documented for emergency events identified through the risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 | Policies and procedures align with identified hazards and response strategies. | ☐ | ☐ | ☐ | ☐ |  |
| E-0036/E-0039 | Training and testing reflect the hazards and capabilities identified in the risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | The risk assessment is revisited when services, location, population, infrastructure, or community risk materially changes. | ☐ | ☐ | ☐ | ☐ |  |

## 3. All-Hazards Coverage

Planning note: The hazard rows below are prompts for the facility- and community-based HVA; CMS does not require a separate policy for every listed hazard. The facility should address hazards identified by its risk assessment and document hazard-specific differences when response strategies differ. For LTC, the risk assessment specifically includes missing residents, and Appendix Z expects emerging infectious disease/pandemic threats to be considered.

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0006 | Severe winter weather / blizzard / ice has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Extreme cold has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Extreme heat has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Flooding has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Severe thunderstorm / high wind has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Wildfire / smoke has been considered where relevant. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Fire has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Hazardous materials release has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Mass casualty / community surge has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Violence / active threat / security incident has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Cyberattack has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Extended IT / EHR downtime has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Telephone / communications failure has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Power failure and generator failure have been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Water interruption has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Sewer / waste interruption has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Heating / fuel interruption has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | HVAC failure has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Medical gas disruption has been considered where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Medical equipment failure has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Loss of all or part of the facility has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Transportation / access disruption has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Supply-chain, pharmaceutical, and medical supply disruption has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Staffing shortage has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Emerging infectious disease / pandemic has been considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Other facility- or community-specific hazards are documented and ranked. | ☐ | ☐ | ☐ | ☐ |  |

## 4. Population Served and Vulnerabilities

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0007 | The EOP identifies the patient/resident/client population served. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Unique vulnerabilities of the population during emergencies are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Mobility and transportation needs are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Medical equipment dependence and life-sustaining treatment needs are considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Communication, language, cognitive, behavioral, and access/functional needs are considered as applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | The plan identifies services the organization can continue during an emergency. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | The plan identifies services that may need to be reduced, suspended, transferred, or relocated. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Continuity or transfer of care is addressed when normal operations cannot be maintained. | ☐ | ☐ | ☐ | ☐ |  |

## 5. Continuity of Operations

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0007 | Essential functions and services are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Essential personnel and staffing functions are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Critical resources, equipment, and supplies are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007/E-0023 | Vital records and critical information are protected and available. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007/E-0023 | Critical IT/data systems and downtime contingencies are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Alternate methods for performing essential functions are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Alternate operating locations are identified when needed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Delegations of authority support continued operations. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Succession plans support continued operations. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Continuity planning addresses extended-duration emergencies. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Triggers for reduction, suspension, relocation, or cessation of services are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0025 ¦ IF APPLICABLE | Arrangements with other providers/facilities support continuity when the organization cannot continue required services. | ☐ | ☐ | ☐ | ☐ |  |

## 6. Delegation of Authority and Emergency Management Structure

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0007 | Delegations of authority are documented. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Succession of leadership is documented. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | Alternate decision-makers are identified for unavailable leaders. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Individuals/positions authorized to activate the EOP are identified. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Activation criteria or levels are defined. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency command/management roles and responsibilities are defined. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Operations, planning/situation status, logistics, finance/administration, public information, and liaison functions are assigned as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037 | Staff assigned emergency roles can describe their responsibilities. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Incident management structure is scalable for events of different size and duration. | ☐ | ☐ | ☐ | ☐ |  |

## 7. Cooperation and Community Integration

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0009 | The EOP includes a process for cooperation and collaboration with local emergency preparedness officials. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009 | Regional emergency preparedness coordination is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009 | State emergency preparedness coordination is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009 | Tribal emergency preparedness coordination is addressed when applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009 | Federal emergency preparedness coordination is addressed as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| E-0031 | Local/county emergency management contact information is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0031 | State/local public health contact information is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0031 | Fire, EMS, law enforcement, and other response partners are identified as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009 ¦ HCC-ME REC | Healthcare Coalition coordination is addressed and documented when used for planning, exercises, or compliance support. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Mutual aid, transfer, transportation, or resource-sharing agreements are identified where applicable. | ☐ | ☐ | ☐ | ☐ |  |

## 8. Emergency Policies and Procedures — Core Framework

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0013 | Emergency policies and procedures are based on the emergency plan. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 | Policies and procedures are based on the facility- and community-based risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 | Policies and procedures are coordinated with the communication plan. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 | LTC emergency preparedness policies and procedures are reviewed and updated at least annually. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 Guidance | Policies identify who initiates the emergency response. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 Guidance | Policies define circumstances for evacuation, sheltering, closure, relocation, or other protective actions as applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 Guidance | Hazard-specific differences are incorporated without unnecessary duplication. | ☐ | ☐ | ☐ | ☐ |  |
| E-0026 | Policies and procedures describe the LTC facility's role under a section 1135 waiver in providing care and treatment at an alternate care site identified by emergency management officials. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Policies/procedures can be accessed during network or EHR downtime. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency procedures include recovery/restoration and return-to-normal operations where applicable. | ☐ | ☐ | ☐ | ☐ |  |

## 9. Evacuation, Relocation, Shelter, and Tracking

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0020 ¦ IF APPLICABLE | Safe evacuation procedures address care/treatment needs of evacuees. | ☐ | ☐ | ☐ | ☐ |  |
| E-0020 ¦ IF APPLICABLE | Staff responsibilities during evacuation are defined. | ☐ | ☐ | ☐ | ☐ |  |
| E-0020 ¦ IF APPLICABLE | Transportation resources and contingencies are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0020 ¦ IF APPLICABLE | Primary and alternate evacuation destinations are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0020 ¦ IF APPLICABLE | Primary and alternate communications with external sources of assistance are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0022 ¦ IF APPLICABLE | Shelter-in-place procedures identify who may remain and under what conditions. | ☐ | ☐ | ☐ | ☐ |  |
| E-0018 ¦ IF APPLICABLE | A system exists to track on-duty staff and patients/residents/clients during an emergency. | ☐ | ☐ | ☐ | ☐ |  |
| E-0018 ¦ IF APPLICABLE | If individuals are relocated, the receiving location is documented as required. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Evacuation/shelter decisions include contingency triggers when the community is also impacted. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Evacuation planning addresses people requiring beds, stretchers, wheelchairs, oxygen, medications, behavioral support, or staff assistance. | ☐ | ☐ | ☐ | ☐ |  |

## 10. Emergency Staffing and Surge

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0024 ¦ IF APPLICABLE | Emergency staffing strategies are documented. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006/E-0024 | Staff shortage contingencies are aligned with the risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0024 ¦ IF APPLICABLE | Use of volunteers is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0024 ¦ IF APPLICABLE | Individuals providing services under arrangement are integrated into emergency operations as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| E-0024 ¦ IF APPLICABLE | The process/role for State or Federally designated healthcare professionals is addressed where required. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency credentialing/privileging processes are addressed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Staff recall, alternate staffing models, fatigue management, lodging, transportation, and staff family support are considered as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Staffing contingencies are scalable for prolonged events. | ☐ | ☐ | ☐ | ☐ |  |

## 11. Medical Records and Information Continuity

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0023 | The emergency documentation system preserves patient/resident/client information. | ☐ | ☐ | ☐ | ☐ |  |
| E-0023 | Confidentiality of protected information is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0023 | Records are secured during emergency operations. | ☐ | ☐ | ☐ | ☐ |  |
| E-0023 | Records remain available to support continuity of care. | ☐ | ☐ | ☐ | ☐ |  |
| E-0033 | A method exists to share information/medical documentation with other healthcare providers as necessary to maintain continuity of care. | ☐ | ☐ | ☐ | ☐ |  |
| E-0033 ¦ Provider-specific | Procedures address release of information during evacuation where required. | ☐ | ☐ | ☐ | ☐ |  |
| E-0033 | Procedures address sharing general condition/location information where permitted and required. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Downtime forms and paper documentation processes are available. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Post-downtime reconciliation/re-entry of records is addressed. | ☐ | ☐ | ☐ | ☐ |  |

## 12. Communication Plan

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0029 | A written emergency communication plan is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0029 | The communication plan complies with applicable Federal, State, and local laws. | ☐ | ☐ | ☐ | ☐ |  |
| E-0029 | The emergency communication plan is reviewed and updated at least annually and when significant changes occur. | ☐ | ☐ | ☐ | ☐ |  |
| E-0030 | Staff contact information is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0030 | Entities providing services under arrangement are included as required. | ☐ | ☐ | ☐ | ☐ |  |
| E-0030 | Patient/resident/client physicians or practitioners are included as required. | ☐ | ☐ | ☐ | ☐ |  |
| E-0030 | Other healthcare facilities/providers are included as required. | ☐ | ☐ | ☐ | ☐ |  |
| E-0030 | Volunteer contacts are included when applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0031 | Federal, State, tribal, regional, and local emergency preparedness contacts are maintained as applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0031 | Other sources of emergency assistance are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0032 | Primary and alternate means of communicating with staff are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0032 | Primary and alternate means of communicating with emergency management agencies are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0032 ¦ HCC-ME REC | Communications contingencies address cellular, internet, and network failure. | ☐ | ☐ | ☐ | ☐ |  |
| E-0034 | The organization can communicate its emergency needs and ability to provide assistance to the authority having jurisdiction / incident command. | ☐ | ☐ | ☐ | ☐ |  |
| E-0034 ¦ Provider-specific | Occupancy/capacity reporting is available where required. | ☐ | ☐ | ☐ | ☐ |  |

## 13. Resources, Supplies, Utilities, and Supply Chain

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0006 | Critical medical/clinical equipment and supplies are identified. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Pharmaceutical and medication supply risks are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | PPE needs and surge considerations are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Critical vendors and alternate sources are identified. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency procurement and purchasing authority are defined. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Water interruption is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Power interruption is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Food interruption is addressed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Fuel/heating interruption is addressed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Medical gas interruption is addressed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0015 ¦ Provider-specific | Subsistence needs and alternate energy are addressed for provider types subject to E-0015. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006/E-0013 | Contingency triggers are identified when critical resources cannot be restored or maintained. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Supply-chain contingencies account for regional or statewide competition for scarce resources. | ☐ | ☐ | ☐ | ☐ |  |

## 14. Cybersecurity and Extended Downtime

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0006 | Cyberattack is addressed in the all-hazards risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Interruption of communications and IT systems is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0023 ¦ HCC-ME REC | Extended EHR/IT downtime procedures support preservation and availability of records. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Paper forms / manual workflows are available for critical clinical and administrative functions. | ☐ | ☐ | ☐ | ☐ |  |
| E-0032 | Alternate communications are identified. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Critical technology dependencies and recovery priorities are documented. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Downtime procedures address medication, laboratory, imaging, registration, scheduling, billing, and other applicable systems. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Cyber/downtime scenarios are incorporated into exercises when indicated by the risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Recovery includes data reconciliation and controlled return to normal systems. | ☐ | ☐ | ☐ | ☐ |  |

## 15. Emerging Infectious Disease / Pandemic Preparedness

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0006 | Emerging infectious disease and pandemic risk are included in the all-hazards assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | PPE surge needs are considered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Screening/testing considerations are addressed as applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | Isolation, cohorting, distancing, or capacity modifications are addressed as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006/E-0024 | Staffing contingencies are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009/E-0031 | Coordination with public health and emergency management is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 Guidance | The organization identifies a process/person for monitoring event-specific public health guidance and communicating operational changes. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Continuity planning addresses prolonged outbreaks and supply constraints. | ☐ | ☐ | ☐ | ☐ |  |

## 16. Training Program

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0036 | A documented emergency preparedness training program is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0036 | The LTC emergency preparedness training and testing program is reviewed and updated at least annually. | ☐ | ☐ | ☐ | ☐ |  |
| E-0036 | Training is based on the EOP and risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0036 | Training incorporates applicable policies/procedures and communication processes. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037 | Initial training is provided to required new and existing staff and other individuals consistent with expected roles. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037 / Appendix Z Guidance | Emergency preparedness training is provided at least annually after initial training. When emergency policies, procedures, or the plan are significantly revised, the facility evaluates and provides additional training on the revised responsibilities/processes as needed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037 | Training documentation is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037 | Staff can demonstrate knowledge of emergency procedures. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037 / Appendix Z Guidance | Additional training on revised emergency processes is documented when significant program changes affect staff roles or response procedures. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Training includes leadership, clinical, nonclinical, facilities, security, IT, communications, and other relevant roles. | ☐ | ☐ | ☐ | ☐ |  |

## 17. Testing, Exercises, and Actual Events

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0039 | Two emergency-plan testing exercises are conducted each year: an annual community-based full-scale exercise (or annual individual facility-based functional exercise when a community exercise is unavailable) plus an additional annual qualifying exercise. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Exercises test the emergency plan. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Exercises reflect hazards identified by the risk assessment. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Exercises test policies/procedures and communications. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Exercise participation and documentation are retained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Community-based exercises are used when required and available. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Facility-based functional exercises are used when permitted/required. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Qualifying actual emergency activations are documented when used under the applicable regulatory exception. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 Guidance | Testing varies hazards/capabilities rather than repeating the same scenario or response process each cycle. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Exercises include appropriate community partners and all relevant shifts/functions over time. | ☐ | ☐ | ☐ | ☐ |  |

## 18. After-Action Review, Improvement, and Integrated Systems

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0039 | Emergency/exercise response is analyzed and documented. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | Gaps and corrective actions are identified. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Strengths and successful practices are documented for sustainment. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Corrective actions are assigned to responsible owners with due dates. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | EOP/policy revisions are made when findings indicate a change is needed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0037/E-0039 | Training is updated when deficiencies identify a training need. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042 ¦ IF APPLICABLE | For integrated healthcare systems, each separately certified facility actively participates in development of the unified program. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042 ¦ IF APPLICABLE | The integrated program accounts for each facility’s unique circumstances, population, and services. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042 ¦ IF APPLICABLE | Each facility can actively use and comply with the integrated program. | ☐ | ☐ | ☐ | ☐ |  |

PART II — FIRE & LIFE SAFETY COMPLIANCE LAYERS Federal CMS Life Safety Code requirements and Maine State Fire Marshal / local AHJ requirements are reviewed separately

|  | Do not substitute this section for an official inspection Part II contains selected EOP-relevant fire/life-safety readiness items. Part II-A addresses the federal CMS Life Safety Code/K-tag layer; Part II-B addresses Maine State Fire Marshal and local authority-having-jurisdiction requirements. The CMS-2786R federal survey is based on the CMS-adopted 2012 Life Safety Code framework, while Maine applies State-adopted rules and NFPA editions that may differ. Complete the applicable official CMS survey form and comply independently with Maine/local AHJ requirements. |
| --- | --- |

PART II-A — CMS LIFE SAFETY CODE / K-TAG READINESS Federal CMS Life Safety Code survey layer; verify the complete applicable CMS-2786 form separately

## DRILLS & EXERCISES — SEPARATE COMPLIANCE REQUIREMENTS

The three requirements below overlap operationally but are separate compliance layers. Completion of one activity does not automatically establish compliance with another.

| Requirement | Frequency | Key documentation / features | Authority |
| --- | --- | --- | --- |
| CMS Emergency Preparedness — §483.73(d)(2) / E-0039 | At least 2 exercises per year | Includes unannounced staff drills using emergency procedures; annual community-based full-scale exercise (or facility-based functional exercise when unavailable) plus an additional annual qualifying exercise; analyze/document response and revise as needed. | Federal CMS EP |
| CMS Life Safety Code — K712 | At least quarterly on each shift | Fire drills include transmission of the fire alarm signal and simulation of emergency fire conditions; expected and unexpected times and varying conditions. | Federal CMS LSC |
| Maine 10-144 CMR Ch. 110 §20.D.2(e) | 12 rehearsal drills each year; ≥3 per shift | Conducted at irregular intervals. Records include date/time, staff performance, results, and corrective measures. | Maine DLC |

If a single drill or exercise is used as evidence for more than one requirement, the facility should document how that activity independently satisfies each applicable standard.

## 19. Fire Emergency Planning and Drills

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K711 | A written fire/emergency plan protects patients and provides for evacuation/relocation. | ☐ | ☐ | ☐ | ☐ |  |
| K711 | Staff duties under the fire plan are defined. | ☐ | ☐ | ☐ | ☐ |  |
| K711 | Employees are periodically instructed and kept informed of their duties under the plan. | ☐ | ☐ | ☐ | ☐ |  |
| K711 | The fire safety plan is readily available as required. | ☐ | ☐ | ☐ | ☐ |  |
| K711 / E-0020 | Fire evacuation/relocation procedures are coordinated with the organization’s EOP. | ☐ | ☐ | ☐ | ☐ |  |
| K712 | Fire drills include transmission of the fire alarm signal and simulation of emergency fire conditions. | ☐ | ☐ | ☐ | ☐ |  |
| K712 | Fire drills are conducted at least quarterly on each shift, at expected and unexpected times and under varying conditions, as required by CMS-2786R K712. | ☐ | ☐ | ☐ | ☐ |  |
| K712 | Drills occur under expected/unexpected times and varying conditions as required. | ☐ | ☐ | ☐ | ☐ |  |
| K712 | Staff demonstrate familiarity with fire response procedures. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Fire drill findings are integrated into corrective actions, training, and EOP revisions as appropriate. | ☐ | ☐ | ☐ | ☐ |  |

## 20. Means of Egress

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K200/K211 | Required aisles, corridors, passageways, exits, and exit discharges are continuously maintained free of obstructions. | ☐ | ☐ | ☐ | ☐ |  |
| K221/K222 | Patient room and egress door locking arrangements comply with applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K223 | Required self-closing/automatic-closing doors function as required. | ☐ | ☐ | ☐ | ☐ |  |
| K232 | Aisle/corridor/ramp widths meet the applicable occupancy requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K233 | Exit and exit-access doors provide required clear width. | ☐ | ☐ | ☐ | ☐ |  |
| K241 | Required number of remote exits is provided for stories/compartments. | ☐ | ☐ | ☐ | ☐ |  |
| K251/K252 | Dead-end corridors and corridor exit access meet applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K253 | Patient sleeping/non-sleeping rooms have required exit access where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| K261 | Travel distances to exits are within applicable limits. | ☐ | ☐ | ☐ | ☐ |  |
| K271 | Exit discharge is maintained and usable in all weather. | ☐ | ☐ | ☐ | ☐ |  |
| K281 | Means of egress illumination is maintained. | ☐ | ☐ | ☐ | ☐ |  |
| K291 | Required emergency lighting is provided and maintained. | ☐ | ☐ | ☐ | ☐ |  |
| K293 | Exit and directional signage is provided and illuminated as required. | ☐ | ☐ | ☐ | ☐ |  |
| E-0020 / HCC-ME REC | Evacuation planning accounts for patients/residents requiring beds, stretchers, wheelchairs, oxygen, or staff assistance. | ☐ | ☐ | ☐ | ☐ |  |

## 21. Fire Alarm and Detection Systems

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K345 | Fire alarm systems are tested and maintained under an approved program. | ☐ | ☐ | ☐ | ☐ |  |
| K345 | Acceptance, maintenance, and testing records are readily available. | ☐ | ☐ | ☐ | ☐ |  |
| K346 | A procedure addresses a fire alarm system that is out of service, including AHJ notification and fire watch/evacuation when required. | ☐ | ☐ | ☐ | ☐ |  |
| K347 | Required smoke detection systems are provided and maintained. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 72 | Maine-adopted fire alarm/signaling requirements are reviewed for applicability. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Alarm impairment procedures are coordinated with the EOP and internal communications plan. | ☐ | ☐ | ☐ | ☐ |  |

## 22. Sprinklers and Fire Suppression

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K351 | Required automatic sprinkler protection is installed for the applicable occupancy/construction type. | ☐ | ☐ | ☐ | ☐ |  |
| K353 | Automatic sprinkler/standpipe systems are inspected, tested, and maintained in accordance with applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K353 | Design, maintenance, inspection, and testing records are retained and available. | ☐ | ☐ | ☐ | ☐ |  |
| K354 | Sprinkler impairment procedures include risk evaluation and required notification. | ☐ | ☐ | ☐ | ☐ |  |
| K354 | Fire watch or evacuation is implemented when required during prolonged sprinkler impairment. | ☐ | ☐ | ☐ | ☐ |  |
| K355 | Portable fire extinguishers are selected, installed, inspected, and maintained in accordance with applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 25 | Maine-adopted water-based fire protection inspection/testing requirements are reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 10 | Maine-adopted portable extinguisher requirements are reviewed. | ☐ | ☐ | ☐ | ☐ |  |

## 23. Compartmentation, Doors, and Smoke Control

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K321 | Hazardous areas are enclosed/protected as required. | ☐ | ☐ | ☐ | ☐ |  |
| K374 | Smoke barrier doors meet applicable construction and operating requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K761 | Fire door assemblies are inspected and tested annually as required by the applicable CMS LSC standard. | ☐ | ☐ | ☐ | ☐ |  |
| K761 | Non-fire-barrier corridor/patient-room/smoke-barrier doors are routinely inspected as part of the maintenance program. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 80 | Maine-adopted fire door/opening protective requirements are reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Deficiencies affecting compartmentation are tracked and corrected promptly. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Temporary barriers or construction conditions are incorporated into emergency procedures when they affect smoke/fire compartments or egress. | ☐ | ☐ | ☐ | ☐ |  |

## 24. Hazardous Areas, Laboratories, Cooking, and Combustibles

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K321 | Boiler/fuel-fired heater rooms are protected as required. | ☐ | ☐ | ☐ | ☐ |  |
| K321 | Laundry, maintenance/paint, soiled linen, trash, and combustible storage areas are protected as applicable. | ☐ | ☐ | ☐ | ☐ |  |
| K322 | Laboratories using hazardous/flammable materials meet applicable separation and protection requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K323 | Anesthetizing locations meet applicable Life Safety Code / NFPA 99 requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K324 | Cooking facilities meet applicable fire protection requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K325 | Alcohol-based hand rub dispenser/storage requirements are met. | ☐ | ☐ | ☐ | ☐ |  |
| K741 | Smoking controls are established and enforced where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| K781 | Portable space heater use complies with applicable healthcare occupancy restrictions. | ☐ | ☐ | ☐ | ☐ |  |
| K791 | Construction, repair, and improvement operations maintain required life safety and egress. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 96 | Maine-adopted commercial cooking fire protection requirements are reviewed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 20 / NFPA 241 (2019) | Construction/alteration/demolition safeguards are reviewed for projects affecting occupied facilities. | ☐ | ☐ | ☐ | ☐ |  |

## 25. Utilities, HVAC, and Electrical Safety

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K511 | Gas systems and electrical wiring/equipment meet applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K521 | HVAC systems meet applicable life-safety requirements and manufacturer specifications. | ☐ | ☐ | ☐ | ☐ |  |
| K914 | Required electrical receptacle/line isolation monitor testing and maintenance are documented where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| K920 | Power strips and extension cords are used in accordance with applicable patient-care electrical requirements. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Utility shutdown and failure procedures are coordinated with clinical operations and the EOP. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Loss of HVAC, heating, water, sewer, fuel, and electrical systems has defined continuity/evacuation triggers. | ☐ | ☐ | ☐ | ☐ |  |

## 26. Essential Electrical / Emergency Power

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0015 ¦ CMS-EP | Alternate sources of energy support required subsistence/safety functions for applicable provider types. | ☐ | ☐ | ☐ | ☐ |  |
| E-0041 ¦ CMS-EP | Emergency/standby power systems are implemented based on the LTC/SNF emergency plan and applicable CMS Life Safety Code/NFPA requirements. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC K918 | The generator/alternate power source and associated equipment can supply required service within applicable time requirements. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC K918 | Generator sets are inspected, exercised, and maintained at the intervals required by the applicable CMS Life Safety Code/NFPA standards; supporting logs are available for survey review. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC K918 | Transfer switches and associated equipment are maintained and tested at the intervals required by the applicable CMS Life Safety Code/NFPA standards. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC K918 | Written maintenance and testing records are readily available. | ☐ | ☐ | ☐ | ☐ |  |
| E-0041 | Generator location requirements are evaluated for new construction/renovation where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0041 | Onsite fuel and fuel-supply continuity are addressed in emergency planning. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency power load prioritization and contingency actions are documented if generator capacity is limited. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 99 | Maine-adopted healthcare electrical system requirements are reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 110 | Maine-adopted emergency/standby power system requirements are reviewed. | ☐ | ☐ | ☐ | ☐ |  |

## 27. Medical Gas / Oxygen / NFPA 99

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| K923 | Cylinder/container storage meets applicable medical gas storage requirements. | ☐ | ☐ | ☐ | ☐ |  |
| K322/K323 | Medical gas use in laboratories/anesthetizing locations meets applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / NFPA 99 | Medical gas/vacuum system design, alarms, maintenance, inspection/testing, and operation are reviewed for applicable facility systems. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency procedures address loss of oxygen/medical gas supply. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Emergency procedures identify alternate supply sources and conservation priorities where clinically appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Staff responsible for medical gas emergency response know shutoff, notification, and safety procedures appropriate to their roles. | ☐ | ☐ | ☐ | ☐ |  |

## PART II-B — MAINE STATE FIRE MARSHAL / LOCAL AHJ OVERLAY
28. Maine State Fire Marshal / Local AHJ Overlay

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ME-FMO | Facility applicability under Maine FMO rules has been confirmed, including the applicable occupancy/use and current State-adopted code editions. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 3 / NFPA 1 (2018) | Maine Fire Prevention Code requirements have been reviewed for applicability to the facility and its operations. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 20 / NFPA 101 (2018) | Maine Life Safety Code requirements have been reviewed for the facility’s occupancy and use. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 15 / NFPA 99 (2021) | Maine healthcare facilities/equipment requirements have been reviewed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 15 / NFPA 110 (2022) | Maine emergency and standby power requirements have been reviewed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 17 / NFPA 72 (2019) | Maine fire alarm/signaling requirements have been reviewed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 4 / NFPA 13/13D/13R/14/20 | Applicable Maine water-based fire protection system installation, standpipe, and fire-pump requirements have been reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 4 / NFPA 25 (2014) | Maine water-based fire protection inspection, testing, and maintenance requirements have been reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 5 / NFPA 10 (2018) | Maine portable fire extinguisher requirements have been reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 20 / NFPA 80 (2019) | Maine fire door/opening protective requirements have been reviewed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 19 / NFPA 96 (2021) | Maine commercial cooking fire protection requirements have been reviewed where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO Ch. 20 / NFPA 241 (2019) | Construction, alteration, and demolition safeguards have been reviewed for projects affecting occupied facilities. | ☐ | ☐ | ☐ | ☐ |  |
| 25 M.R.S. §2448 / ME-FMO | Required State Fire Marshal or delegated-municipality construction permits and plan review have been obtained before constructing, altering, or changing the use of a covered public building. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / LOCAL AHJ | Current inspection reports are retained and outstanding deficiencies have corrective-action plans. | ☐ | ☐ | ☐ | ☐ |  |

## 29. Fire / Life-Safety Documentation Readiness

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| CMS-LSC | The correct CMS-2786 survey form for the facility’s occupancy/provider type has been identified. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC | The applicable CMS-2786 survey form is completed/reviewed separately from this checklist. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC | Fire alarm, sprinkler, generator, door, extinguisher, and other required inspection/testing records are readily retrievable. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO | Maine FMO inspection/permit documentation is retained where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| LOCAL AHJ | Local fire department/AHJ inspection and impairment records are retained where applicable. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Life-safety deficiencies that affect emergency operations are reflected in the EOP until corrected. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Facilities, emergency management, clinical leadership, and administration jointly review high-risk life-safety findings that affect continuity or evacuation. | ☐ | ☐ | ☐ | ☐ |  |

PART III — LONG-TERM CARE / SKILLED NURSING FACILITY-SPECIFIC REQUIREMENTS LTC/SNF summary crosswalk; complete Part I and both Part II compliance layers in addition to this section

LONG-TERM CARE / SKILLED NURSING FACILITY — CMS EMERGENCY PREPAREDNESS 42 CFR §483.73 ¦ CMS Appendix Z ¦ Maine facilities are also subject to 10-144 CMR Ch. 110

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| E-0004 | The LTC emergency preparedness plan is reviewed and updated at least annually. | ☐ | ☐ | ☐ | ☐ |  |
| E-0006 | The facility- and community-based risk assessment uses an all-hazards approach and includes hazards relevant to LTC residents, including missing residents. | ☐ | ☐ | ☐ | ☐ |  |
| E-0007 | The emergency plan addresses the resident population and vulnerabilities; services/capabilities; continuity of operations; delegations of authority; and succession planning. | ☐ | ☐ | ☐ | ☐ |  |
| E-0009 | The emergency plan includes a process for cooperation and collaboration with local, tribal, regional, State, and Federal emergency preparedness officials to support an integrated response. | ☐ | ☐ | ☐ | ☐ |  |
| E-0013 | Emergency preparedness policies and procedures are based on the emergency plan, risk assessment, and communication plan and are reviewed/updated at least annually. | ☐ | ☐ | ☐ | ☐ |  |
| E-0015 | Subsistence and alternate-energy policies address food, water, medical/pharmaceutical supplies, safe temperatures, emergency lighting, fire detection/extinguishing/alarm systems, and sewage/waste disposal. | ☐ | ☐ | ☐ | ☐ |  |
| E-0018 | Procedures track on-duty staff and sheltered residents during and after an emergency and document the specific name/location of any receiving facility or other relocation location. | ☐ | ☐ | ☐ | ☐ |  |
| E-0020 | Safe evacuation procedures address resident care/treatment needs, staff responsibilities, transportation, evacuation locations, and primary/alternate means of communication with external assistance. | ☐ | ☐ | ☐ | ☐ |  |
| E-0022 | Shelter-in-place procedures identify how residents, staff, and volunteers who remain in the facility will be protected. | ☐ | ☐ | ☐ | ☐ |  |
| E-0023 | Policies and procedures preserve resident medical documentation, protect confidentiality, and secure and maintain record availability during an emergency. | ☐ | ☐ | ☐ | ☐ |  |
| E-0024 | Emergency staffing strategies address volunteers and other staffing strategies, including integration of State/Federally designated health care professionals to address surge needs when applicable. | ☐ | ☐ | ☐ | ☐ |  |
| E-0025 | Arrangements with other LTC facilities/providers support continuity of resident care if the facility experiences limitations or cessation of operations. | ☐ | ☐ | ☐ | ☐ |  |
| E-0026 | Policies and procedures describe the facility's role under a section 1135 waiver in providing care/treatment at an alternate care site identified by emergency management officials. | ☐ | ☐ | ☐ | ☐ |  |
| E-0029 | A written emergency communication plan is maintained, complies with Federal/State/local law, and is reviewed/updated at least annually. | ☐ | ☐ | ☐ | ☐ |  |
| E-0030 | The communication plan maintains names/contact information for staff, entities providing services under arrangement, residents' physicians, other LTC facilities, and volunteers. | ☐ | ☐ | ☐ | ☐ |  |
| E-0031 | The communication plan includes Federal, State, tribal, regional, and local emergency preparedness contacts; the State licensing/certification agency; the Long-Term Care Ombudsman; and other sources of assistance. | ☐ | ☐ | ☐ | ☐ |  |
| E-0032 | Primary and alternate means are identified for communicating with facility staff and Federal/State/tribal/regional/local emergency management agencies. | ☐ | ☐ | ☐ | ☐ |  |
| E-0033 | The plan addresses sharing resident information/medical documentation with other health care providers for continuity of care; permitted release during evacuation; and permitted sharing of general condition/location information. | ☐ | ☐ | ☐ | ☐ |  |
| E-0034 | A method is established to communicate facility occupancy, needs, and ability to provide assistance to the authority having jurisdiction, Incident Command Center, or designee. | ☐ | ☐ | ☐ | ☐ |  |
| E-0035 | A method is established to share emergency-plan information the facility determines appropriate with residents and their families/representatives. | ☐ | ☐ | ☐ | ☐ |  |
| E-0036/E-0037 | The written training and testing program is reviewed/updated at least annually. Initial and annual emergency preparedness training is provided to required staff, individuals providing services under arrangement, and volunteers; documentation and staff knowledge are maintained. | ☐ | ☐ | ☐ | ☐ |  |
| E-0039 | The LTC facility conducts at least two emergency-plan exercises each year, including unannounced staff drills: an annual community-based full-scale exercise (or facility-based functional exercise when a community exercise is unavailable) and an additional annual qualifying exercise. Response is analyzed/documented and the plan is revised as needed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0041 | Emergency/standby power systems are implemented based on the emergency plan. Applicable generator location, inspection/testing/maintenance, and onsite-fuel continuity requirements are addressed. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042(f)(1) ¦ IF APPLICABLE | Each separately certified facility actively participates in development of the unified and integrated emergency preparedness program. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042(f)(2) ¦ IF APPLICABLE | The integrated program accounts for each separately certified facility's unique circumstances, patient/resident populations, and services offered. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042(f)(3) ¦ IF APPLICABLE | Each separately certified facility can actively use and comply with the unified and integrated emergency preparedness program. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042(f)(4) ¦ IF APPLICABLE | The unified emergency plan meets §483.73(a)(2)-(4) and is based on a documented community-based risk assessment plus a documented facility-based risk assessment for each separately certified facility. | ☐ | ☐ | ☐ | ☐ |  |
| E-0042(f)(5) ¦ IF APPLICABLE | The integrated program includes policies/procedures meeting §483.73(b), a coordinated communication plan meeting §483.73(c), and training/testing programs meeting §483.73(d). | ☐ | ☐ | ☐ | ☐ |  |
| 42 CFR §483.73(g) | The facility identifies and applies the Federal NFPA standards incorporated by reference in §483.73(g), including the CMS-referenced editions of NFPA 99, NFPA 101, and NFPA 110, as applicable. | ☐ | ☐ | ☐ | ☐ |  |
| CROSS-REG / E-0001 | Applicable Federal, State of Maine, local, Life Safety Code, physical-environment, infection-control, licensure, and organizational requirements are reviewed through the appropriate compliance layer. | ☐ | ☐ | ☐ | ☐ |  |
| CMS-LSC | The applicable CMS 2012 Life Safety Code requirements and CMS-2786R fire safety survey requirements for the LTC/SNF health care occupancy are reviewed separately from this EOP-readiness crosswalk. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / LOCAL AHJ | Current Maine State Fire Marshal rules, State-adopted NFPA standards, permits/inspection requirements, and local AHJ requirements are reviewed separately from the federal CMS Life Safety Code layer. | ☐ | ☐ | ☐ | ☐ |  |

MAINE LONG-TERM CARE / SKILLED NURSING FACILITY ADDITIONAL REQUIREMENTS 10-144 CMR Ch. 110 — Regulations Governing the Licensing and Functioning of Skilled Nursing Facilities and Nursing Facilities

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ME-DLC Ch. 110 §5.A-§5.B | Written facility policies are reviewed at least annually through the professional policy group/quality-assurance process and include applicable emergency, outside-resource agreement, resident-record, infection-control/waste, disaster-preparedness, and staff orientation/in-service policies. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §8.C.3(c),(e) | At least one in-service education program each year relates to disaster preparedness, and records document the content and staff participation. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §18.A.1(m) | Dietetic policies and procedures include a disaster feeding plan. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §18.F.1 | The facility maintains on the premises at least a one-week supply of staple foods and 48 hours of perishable foods sufficient to meet the planned menu. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.B.4 | For new facilities, facilities changing ownership, or major renovations requiring a Certificate of Need, the facility provides the emergency generator required by Maine Ch. 110. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.B.5(a) | During electrical power outages, continuing emergency power (electrical or otherwise) supports required essential services: fire detection/alarm, telephone, boiler burners/fans/pumps, exit/corridor lights, call systems, nurses-station lights, food preparation, required heat, water-supply pumps, and private septic pumps. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.B.5(b) | When life-support equipment or life-support systems are used, sufficient emergency electrical power is available for safe uninterrupted operation through an on-premises emergency generator. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.C.2(h) | Driveways, parking areas, exterior walkways, fire lanes, ramps, stairs, and means of egress are maintained free of ice, snow, debris, and other hazards. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.1 | The facility maintains required State of Maine Department of Public Safety certification for compliance with fire protection and prevention requirements. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(a) | A written disaster and emergency preparedness plan and procedures meet facility needs and identify the emergencies and disasters most likely to occur. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(a)(1) | The plan addresses disasters within the facility that may require moving residents within the facility or to another building/community location, including fire, loss of heat/power/water, structural damage, and other internal events; the plan specifies emergency-power sources and methods. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(a)(2) | The plan addresses disasters outside the facility/community that may not require resident relocation but require continuity of heat, lights, and food, including contingencies when an emergency generator is not available. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(a)(3) | The plan addresses other potential emergencies, including severe weather and missing residents. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(b) | A copy of the disaster plan is provided to the Maine Department of Health and Human Services, and revisions are submitted when they occur. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(c) | Employees receive training when they begin work in the use of firefighting equipment and evacuation of residents from fire and other emergencies; orientation to the Disaster and Emergency Preparedness Plan occurs upon employment, with annual training thereafter. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(d) | Fire regulations and evacuation plans are posted conspicuously on each floor of each section of the facility and identify emergency steps to take upon discovery of a fire. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.2(e) | Disaster-plan rehearsal drills are conducted at irregular intervals twelve times each year, with at least three drills per year for each shift. Records show date/time, staff performance, results, and corrective measures. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.3 | Any smoke or fire incident involving the facility or a resident is reported immediately by verbal report followed by a written report to the Department and the State Fire Marshal, including date, time, place, description, and action taken. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.4(a)-(b) | The manual fire alarm system is tested at least monthly and emergency lights are checked at least monthly. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.4(c)-(d) | The sprinkler system is checked by a qualified sprinkler service person at least annually, and fire extinguishers are checked/tagged at least annually or more often as indicated. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.4(e) | The emergency generator is made operational for at least one-half hour each month. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §20.D.4(f)-(g) | A record book documents required equipment tests/checks, including date, person performing the check, and results; defective equipment is repaired as soon as possible. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §21.A.1 | The infection-control program includes required consultation/reporting to the Maine CDC for mandatory reportable disease events and required coordination with DLC regarding universal testing and resident cohorting. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §21.A.2 | A written crisis staffing plan includes a clear process to recruit personnel without relying on National Guard or other government resources as the primary or secondary crisis-staffing source and outlines a progression of facility interventions during a disease outbreak. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC Ch. 110 §21.A.4(f) | The facility maintains personal protective equipment sufficient to last at least 72 hours on hand at all times and reports PPE resources to the Maine CDC in the format and frequency it specifies. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC / Construction | For nursing-facility construction or renovations, applicable Certificate of Need requirements are addressed; architectural plans are submitted electronically to both the State Fire Marshal and DLC, and required architect certification is submitted to DLC. | ☐ | ☐ | ☐ | ☐ |  |

PART IV — MAINE & ACCREDITATION VERIFICATION Confirm regulatory layers beyond the CMS Appendix Z core for this Long-Term Care / Skilled Nursing Facility

## 30. Maine Compliance Verification

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ME-DLC | Applicable Maine DHHS/DLC licensing rule(s) have been identified for the organization and each site. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC | The EOP and supporting policies have been compared with applicable Maine licensing requirements. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO | Maine State Fire Marshal applicability and current rule/code editions have been confirmed. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO | Applicable FMO inspection, permit, plan review, and deficiency documentation is current. | ☐ | ☐ | ☐ | ☐ |  |
| LOCAL AHJ | Local fire/building/AHJ requirements have been evaluated. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | County/local EMA coordination is documented. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Maine CDC/public health coordination is addressed. | ☐ | ☐ | ☐ | ☐ |  |
| HCC-ME REC | Healthcare Coalition of Maine coordination/contact information is incorporated as appropriate. | ☐ | ☐ | ☐ | ☐ |  |
| ME-DLC / IF APPLICABLE | Separate reporting requirements (e.g., sentinel events or other regulatory notifications) are coordinated with emergency procedures where relevant. | ☐ | ☐ | ☐ | ☐ |  |
| ME-FMO / ME-DLC | Construction/renovation/change-of-use requirements have been reviewed with FMO/DLC when applicable. | ☐ | ☐ | ☐ | ☐ |  |

## 31. Accreditation Overlay — If Applicable

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| ACCRED | Current accreditation emergency management standards have been identified. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Accreditation requirements exceeding CMS minimums are identified. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Leadership and governance requirements are crosswalked. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | HVA/risk assessment requirements are crosswalked. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Emergency policies/procedures requirements are crosswalked. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Communication requirements are crosswalked. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Training and exercise requirements are crosswalked. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Continuity/recovery requirements are crosswalked. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Physical environment/life-safety accreditation requirements are crosswalked separately. | ☐ | ☐ | ☐ | ☐ |  |
| ACCRED | Accreditation evidence-retention requirements are addressed. | ☐ | ☐ | ☐ | ☐ |  |

PART V — COMPLIANCE CROSSWALK & CORRECTIVE ACTION Use these pages to document evidence locations and track unresolved gaps Use these pages to document evidence locations and track unresolved gaps

## Master evidence crosswalk

| Item ID | Requirement / Finding | EOP / Policy / Evidence Location | Status | Owner | Last Review / Due |
| --- | --- | --- | --- | --- | --- |

## Corrective action log

| Finding / ID | Risk | Corrective Action | Owner | Due Date | Closure / Evidence |
| --- | --- | --- | --- | --- | --- |

FINAL REVIEW & SIGN-OFF Document completion and leadership review

| ID | Requirement | Met | Partial | Not Met | N/A | EOP Location / Evidence / Notes |
| --- | --- | --- | --- | --- | --- | --- |
| FINAL | Universal CMS section completed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Long-Term Care / Skilled Nursing Facility-specific requirements completed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Applicable CMS Appendix Z E-tags reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Applicable CMS Life Safety Code / CMS-2786 requirements reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Maine FMO requirements reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Applicable Maine DLC rule(s) reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Local AHJ requirements reviewed. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Accreditation requirements reviewed if applicable. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | EOP locations/evidence documented for applicable requirements. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Outstanding gaps have corrective-action plans. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Required training has been completed/documented. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Required exercises have been completed/documented. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | After-action/improvement activities have been incorporated. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | Leadership has reviewed the completed assessment. | ☐ | ☐ | ☐ | ☐ |  |
| FINAL | CMS E-0039 exercises, CMS K712 fire drills, and Maine Ch. 110 §20.D.2(e) disaster-plan rehearsal drills have each been evaluated and documented as separate requirements. | ☐ | ☐ | ☐ | ☐ |  |

| Reviewer | Signature / Name | Field | Entry |
| --- | --- | --- | --- |
| Emergency Preparedness Lead |  | Date |  |
| Facility Administrator / Executive |  | Date |  |
| Safety / Facilities Representative |  | Date |  |
| Clinical Representative |  | Date |  |
| Additional Reviewer |  | Date |  |

SOURCE & VERSION REFERENCES Primary sources used to build the Long-Term Care / Skilled Nursing Facility checklist

|  | Version control Regulations, CMS guidance, Maine rules, and adopted code editions can change. Verify the current source before using this checklist as the sole basis for a compliance decision. |
| --- | --- |

| Source | Use / Version | Official Link |
| --- | --- | --- |
| CMS State Operations Manual, Appendix Z — Emergency Preparedness for All Provider and Certified Supplier Types | Appendix Z, Rev. 204 (04/16/2021), used for LTC emergency preparedness E-tags and interpretive guidance. | Open official source |
| CMS Form 2786R — Fire Safety Survey Report, 2012 Life Safety Code, Healthcare | Form CMS-2786R (07/2018); applicable health care occupancy Life Safety Code survey crosswalk. | Open official source |
| Electronic Code of Federal Regulations — Long-Term Care Emergency Preparedness | 42 CFR §483.73; current LTC regulatory text verified September 14, 2026. | Open official source |
| Maine DHHS Division of Licensing and Certification — Rules & Regulations | Identifies 10-144 CMR Ch. 110 for Skilled Nursing Facilities and Nursing Facilities and other applicable Maine healthcare rules. | Open official source |
| Maine 10-144 CMR Ch. 110 — Regulations Governing the Licensing and Functioning of Skilled Nursing Facilities and Nursing Facilities | Current Maine rule used for LTC/SNF disaster planning, emergency power, drills, fire reporting/testing, infection-control coordination, and crisis staffing requirements. | Open official source |
| Maine DHHS DLC — Nursing Facilities | Current Maine DLC page identifying LTC/SNF federal regulations, Ch. 110, Life Safety Code applicability, licensure, and construction/renovation requirements. | Open official source |
| Maine Office of State Fire Marshal — Rules | Current Maine FMO rule chapters governing fire and life safety; reviewed September 14, 2026. | Open official source |
| Maine Office of State Fire Marshal — State Adopted NFPA Standards | Current State-adopted NFPA editions; reviewed September 14, 2026. | Open official source |
| Maine Office of State Fire Marshal — Construction / Plans Review | Construction permit and plan-review requirements for covered public/healthcare facilities. | Open official source |
| ASPR TRACIE — CMS Emergency Preparedness Rule / Facility-Specific Requirement Overviews | Facility-specific CMS Emergency Preparedness Rule overview used as a secondary validation source for LTC requirements. | Open official source |
| Maine Revised Statutes — 25 M.R.S. §2448 Construction Permit; When Required | Requires a construction permit before constructing, altering, or changing the use of a covered public building, subject to the statute. | Open official source |

HCC-ME DOCUMENT NOTE: This Long-Term Care / Skilled Nursing Facility checklist should be reviewed whenever CMS emergency preparedness regulations, Appendix Z guidance, Maine 10-144 CMR Ch. 110, Maine State Fire Marshal rules, applicable NFPA editions, or accreditation standards change. Current provider-specific requirements control if they differ from this checklist.

# APPENDIX A — LTC/SNF POLICIES & PROCEDURES CROSSWALK

Quick-reference index of the policies, procedures, plans, and supporting documents that a Maine long-term care / skilled nursing facility should be able to identify when completing this compliance checklist.

| HOW TO USE | This appendix does not require a separate stand-alone policy for every row. A facility may address a requirement within the EOP, a department policy, a procedure, an annex, or another controlled document, provided the applicable regulatory elements are fully addressed and evidence can be produced. Use the final two columns to identify the facility document/location and current status. |
| --- | --- |

| Policy / Procedure Area | CMS Authority | Maine Authority | Minimum Elements / Evidence to Identify | Facility Document / EOP Location | Status |
| --- | --- | --- | --- | --- | --- |
| Emergency preparedness program governance & annual review | 42 CFR §483.73; E-0001, E-0004 | Ch. 110 §5.A–§5.B | Written program and EOP; responsible leadership; annual review/update; version/revision control; compliance with applicable Federal, State, and local requirements. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Facility- and community-based risk assessment / HVA | §483.73(a)(1); E-0006 | Ch. 110 §20.D.2(a) | Documented all-hazards risk assessment addressing facility and community risks, including missing residents, utility/equipment failure, severe weather, infectious disease, cyber/communications disruption, and other locally relevant hazards. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Resident population, capabilities & continuity of operations | §483.73(a)(3); E-0007 | Ch. 110 §20.D.2(a) | Resident vulnerabilities and care needs; services the facility can continue; delegations of authority; succession; continuity/relocation triggers. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Coordination with emergency preparedness officials | §483.73(a)(4); E-0009 | — | Process for cooperation/collaboration with local, tribal, regional, State, and Federal emergency preparedness officials and community partners. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency policies & procedures framework | §483.73(b); E-0013 | Ch. 110 §5.A–§5.B | Policies/procedures based on the emergency plan, risk assessment, and communication plan; annual review/update; clear activation authority and protective-action decision points. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Subsistence needs & alternate energy | §483.73(b)(1); E-0015 | Ch. 110 §18.A.1(m), §18.F.1, §20.B.5 | Food, water, medical/pharmaceutical supplies; safe temperatures; emergency lighting; fire detection/alarm/extinguishing; sewage/waste; disaster feeding and required food supplies; alternate energy. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Resident & on-duty staff tracking | §483.73(b)(2); E-0018 | — | Method to track on-duty staff and sheltered residents during/after an emergency; record specific receiving location when residents/staff are relocated. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Evacuation & relocation | §483.73(b)(3); E-0020 | Ch. 110 §20.D.2(a)(1), §20.D.2(c)-(d) | Resident care/treatment needs; staff roles; transportation; primary/alternate destinations; external assistance; fire and other emergency evacuation; posted evacuation information. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Shelter-in-place | §483.73(b)(4); E-0022 | Ch. 110 §20.D.2(a)(2) | Procedures to protect residents, staff, and volunteers who remain in place; continuity of heat, lights, food, water, medications, sanitation, and essential services. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Resident medical documentation & confidentiality | §483.73(b)(5); E-0023 | Ch. 110 §5.A–§5.B | Preserve resident information; protect confidentiality; secure and maintain availability of records; support continuity of care during downtime/evacuation. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency staffing, volunteers & surge staffing | §483.73(b)(6); E-0024 | Ch. 110 §21.A.2 | Emergency staffing strategies; volunteer integration; contracted/arranged services; credentialing/role considerations; crisis staffing progression. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Continuity arrangements with other facilities / providers | §483.73(b)(7); E-0025 | Ch. 110 §5.A–§5.B | Arrangements or agreements for receiving residents, continuity of services, transportation, resource sharing, and transfer when facility operations are limited or cease. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| 1135 waiver / alternate care site role | §483.73(b)(8); E-0026 | — | Facility role in providing care/treatment at an alternate care site identified by emergency management officials during an applicable §1135 waiver. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency communication plan — required contacts | §483.73(c); E-0029–E-0031 | — | Current contacts for staff, service entities, physicians/practitioners, other LTC facilities, volunteers, emergency preparedness officials, State licensing/certification agency, LTC Ombudsman, and other assistance sources. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Primary & alternate communications / communications failure | §483.73(c)(3); E-0032 | — | Primary and alternate methods for staff and emergency-management communications; contingencies for cellular, internet, network, or other communication-system failure. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Information sharing & resident information release | §483.73(c)(4)-(6); E-0033 | — | Method to share medical documentation for continuity of care; permitted release of resident information during evacuation; general condition/location information. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Facility occupancy, needs & ability-to-assist reporting | §483.73(c)(7); E-0034 | — | Method to provide occupancy/capacity, needs, and ability to provide assistance to the AHJ, incident command center, or designee. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Resident/family emergency-plan information | §483.73(c)(8); E-0035 | — | Method for sharing facility-determined appropriate emergency-plan information with residents and families/representatives. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency preparedness training program | §483.73(d)(1); E-0036, E-0037 | Ch. 110 §8.C.3(c),(e), §20.D.2(c) | Initial training for staff, individuals under arrangement, and volunteers; annual LTC training; documented completion and staff knowledge; Maine disaster-preparedness in-service and fire/evacuation orientation. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| CMS emergency preparedness testing/exercises | §483.73(d)(2); E-0039 | — | At least two EP exercises per year for LTC, including unannounced staff drills; annual community-based full-scale or facility functional exercise (subject to actual-event exception) plus an additional qualifying annual exercise; analysis/AAR and plan revision. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Fire emergency plan & CMS fire drills | CMS LSC K711, K712 | Ch. 110 §20.D.2(c)-(d) | Written fire/emergency plan; staff duties and instruction; fire alarm transmission/simulation; CMS fire drills at least quarterly on each shift at expected and unexpected times/conditions; coordinate with EOP. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Maine disaster-plan rehearsal drills | — | Ch. 110 §20.D.2(e) | Rehearsal drills at irregular intervals 12 times per year, with at least three per shift; records include date/time, staff performance, results, and corrective measures. This is separate from CMS E-0039 and K712. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Fire/smoke incident reporting & fire-safety testing records | CMS LSC as applicable | Ch. 110 §20.D.3, §20.D.4(a)-(g) | Immediate verbal then written smoke/fire incident reporting; required fire alarm, emergency-light, sprinkler, extinguisher, generator and related tests/checks; record book and prompt repair of deficiencies. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Emergency/standby power & generator continuity | §483.73(e); E-0041; CMS LSC K918 | Ch. 110 §20.B.4–§20.B.5, §20.D.4(e)-(g) | Power systems based on plan/risk; essential loads; life-support power where applicable; generator location/inspection/testing/maintenance/fuel continuity; Maine monthly generator operation and records. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Infection control / emerging infectious disease coordination | E-0006, E-0013; applicable infection-control rules | Ch. 110 §21.A.1 | EID/pandemic risk; public-health monitoring/coordination; reporting/consultation; testing/cohorting processes as required; operational changes linked to EOP. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| PPE continuity & outbreak resource planning | E-0006 / E-0015 as applicable | Ch. 110 §21.A.4(f) | PPE surge/continuity planning; Maine minimum on-hand PPE requirement and Maine CDC resource reporting as specified; supply-chain contingencies. |  | ☐ M ☐ P ☐ NM ☐ N/A |
| Construction / renovation / impairment emergency procedures | CMS LSC / E-0041 as applicable | 25 M.R.S. §2448; ME-FMO / Ch. 110 construction requirements | Plan review/permit coordination; temporary barriers/impairments; egress and fire-protection continuity; generator/EPSS implications; FMO/DLC review where applicable. |  | ☐ M ☐ P ☐ NM ☐ N/A |

# APPENDIX B — LTC/SNF REGULATORY CROSSWALK

Topic-level crosswalk showing where the principal federal CMS emergency preparedness, federal CMS Life Safety Code, Maine DHHS/DLC, and Maine State Fire Marshal requirements intersect. Use this as a navigation aid with the detailed checklist; it is not a substitute for the controlling regulation, survey form, code, or AHJ determination.

| REGULATORY LAYERS | CMS Emergency Preparedness E-tags, CMS Life Safety Code K-tags, Maine DHHS/DLC Chapter 110 requirements, and Maine State Fire Marshal / local AHJ requirements are separate compliance layers. A single facility activity may support more than one layer only when the activity and documentation satisfy each applicable requirement. |
| --- | --- |

| Topic | CMS Emergency Preparedness | CMS Life Safety / K-Tag Layer | Maine DHHS / DLC | Maine FMO / State-Adopted Code Layer | Facility Evidence / Notes |
| --- | --- | --- | --- | --- | --- |
| Program administration & annual review | 42 CFR §483.73; E-0001, E-0004 | — | Ch. 110 §5.A–§5.B | Applicable State/local requirements |  |
| Risk assessment / HVA | §483.73(a)(1); E-0006 | Supports evacuation/power/life-safety planning | Ch. 110 §20.D.2(a) | Hazards affecting occupancy, fire/life safety, utilities, and emergency power |  |
| Resident population & continuity | §483.73(a)(3); E-0007 | Life-safety/egress considerations for resident acuity and mobility | Ch. 110 §20.D.2(a) | NFPA 101 (Maine-adopted edition) and applicable occupancy/use requirements |  |
| Government/community coordination | §483.73(a)(4); E-0009 | AHJ coordination where life-safety systems are impaired | As applicable | Local fire department / AHJ / FMO coordination |  |
| Policies & procedures | §483.73(b); E-0013 | Policies supporting LSC compliance/impairments as applicable | Ch. 110 §5.A–§5.B | State-adopted fire/life-safety requirements as applicable |  |
| Subsistence & alternate energy | §483.73(b)(1); E-0015 | K918 and applicable electrical/emergency power requirements | Ch. 110 §18.A.1(m), §18.F.1, §20.B.5 | ME-FMO Ch. 15 / NFPA 99 (2021), NFPA 110 (2022) as applicable |  |
| Tracking / relocation | §483.73(b)(2); E-0018 | Supports evacuation/relocation accountability | — | Applicable AHJ/incident coordination |  |
| Evacuation / shelter-in-place | §483.73(b)(3)-(4); E-0020, E-0022 | K711; means of egress K200-series; K291 emergency lighting | Ch. 110 §20.D.2(a)-(d) | ME-FMO Ch. 20 / NFPA 101 (2018); local AHJ requirements |  |
| Resident records / continuity of care | §483.73(b)(5); E-0023 | — | Ch. 110 §5.A–§5.B | — |  |
| Staffing / volunteers / surge | §483.73(b)(6); E-0024 | — | Ch. 110 §21.A.2 | — |  |
| Receiving arrangements / alternate care site | §483.73(b)(7)-(8); E-0025, E-0026 | — | Ch. 110 §5.A–§5.B as applicable | — |  |
| Communication plan | §483.73(c); E-0029–E-0035 | AHJ notification requirements for impairments as applicable | — | Local AHJ / FMO communications for alarms, impairments, fire incidents, permits as applicable |  |
| Emergency preparedness training | §483.73(d)(1); E-0036, E-0037 | K711 staff duties/instruction | Ch. 110 §8.C.3(c),(e), §20.D.2(c) | Applicable fire-safety training / AHJ expectations |  |
| CMS EP exercises | §483.73(d)(2); E-0039 — two exercises/year for LTC | Separate from K712 fire-drill requirement | — | — |  |
| Fire drills / disaster rehearsal drills | E-0039 may include drills but is a distinct EP requirement | K712 — at least quarterly on each shift; expected/unexpected times and varying conditions | Ch. 110 §20.D.2(e) — 12 irregular-interval rehearsal drills/year; ≥3 per shift | Applicable FMO/local AHJ fire-safety requirements |  |
| Fire emergency plan | Coordinates with E-0020/E-0022 and facility EOP | K711 written fire/emergency plan | Ch. 110 §20.D.2(c)-(d) | ME-FMO Ch. 20 / NFPA 101 (2018) |  |
| Fire alarm / detection | Supports E-0015 alternate energy and emergency operations | K345–K347 | Ch. 110 §20.D.4(a) | ME-FMO Ch. 17 / NFPA 72 (2019) |  |
| Sprinklers / suppression / extinguishers | Supports E-0015 and continuity | K351–K355 | Ch. 110 §20.D.4(c)-(d) | ME-FMO Ch. 4 / NFPA 13/13D/13R/14/20; NFPA 25 (2014); Ch. 5 / NFPA 10 (2018) |  |
| Doors / compartmentation / egress | Supports evacuation/shelter strategies | K200-series, K321, K374, K761 and applicable tags | Ch. 110 §20.C.2(h), §20.D.1 | ME-FMO Ch. 20 / NFPA 101 (2018), NFPA 80 (2019) |  |
| Emergency/standby power | §483.73(e); E-0041 | K918 and applicable CMS LSC/NFPA requirements | Ch. 110 §20.B.4–§20.B.5; §20.D.4(e)-(g) | ME-FMO Ch. 15 / NFPA 99 (2021), NFPA 110 (2022) |  |
| Medical gas / oxygen | Risk assessment, utilities, continuity and E-0015 as applicable | K923 and applicable K-tags | As applicable under facility operations | ME-FMO Ch. 15 / NFPA 99 (2021) |  |
| Smoke/fire incident reporting & equipment records | — | LSC inspection/testing documentation as applicable | Ch. 110 §20.D.3–§20.D.4 | FMO/local AHJ reporting, inspection and documentation requirements as applicable |  |
| Infection control / outbreak readiness | E-0006/E-0013 and related EP program elements | — | Ch. 110 §21.A.1, §21.A.2, §21.A.4(f) | — |  |
| Construction / renovation / change of use | E-0041 when emergency power/EPSS is affected | Applicable CMS LSC requirements | Ch. 110 construction/DLC review requirements | 25 M.R.S. §2448; FMO plan review/permit; NFPA 241 (2019) as applicable |  |
| Integrated healthcare system EP program | §483.73(f); E-0042 | Facility still must meet applicable LSC requirements | State requirements remain facility-specific | State/local fire/life-safety requirements remain facility-specific |  |
| Standards incorporated by reference | §483.73(g) | Federal CMS LSC is based on CMS-adopted code editions | Maine licensing requirements apply separately | Maine uses State-adopted NFPA editions; verify current FMO list |  |

HCC-ME CROSSWALK NOTE: These appendices summarize and organize requirements already addressed in the detailed checklist. Current provider-specific Federal and State requirements, CMS survey guidance, State Fire Marshal rules, State-adopted code editions, and local AHJ determinations control if they differ from this crosswalk.